## Figures
SAMTMY2020 model results - Row 2+4 | [7 empty] | SAMTMYA01 model results - Row 2+4
Row | Method | ASTM / IEC | MBE | RMSE | MAX | MIN |  | Row | Method | ASTM / IEC | MBE | RMSE | MIN | MAX |  | NEW Refmod is 2.3% lower than Gtotal based on back covered field comparison. | OLD Refmod is 3.5% higher than Gtotal based on Spire point
8 | Tamb | ASTM | -0.01 | 1.32 | 1.0261 | 0.97066 | <- Mono baseline | 8 | Tamb | ASTM | -0.02 | 1.31 |  |  | <- Mono baseline
8 | Tmod | ASTM | 0.65 | 1.64 |  |  |  | 8 | Tmod | ASTM | 0.63 | 1.63
2+4 | POA | ASTM | 1.26 | 2.58 | 1.0926 | 0.94613 | <- Bifacial baseline ? | 2+4 | POA | ASTM | 0.96 | 2.32 | 0.95472 | 1.095 | <- Method 1
2+4 | Gtotal | ASTM | -1.59 | 1.27 | 1.01 | 0.95223 | <- Method 2 | 2+4 | Gtotal | ASTM | -1.56 | 1.32 |  |  | <- Method 2
2+4 | Method4 | ASTM | -0.8 | 0.89 | 1.0201 | 0.97512 | <- Method 4 | 2+4 | Method4 | ASTM | -0.77 | 0.88 |  |  | <- Method 4
2+4 | Method4Min | ASTM | 0.88 | 1.32 |  |  | <- Method 4_min
SAMP11 (CM11 POA and monthly albedo) - row 2+4
[7 empty] | ` | Row | Method | ASTM / IEC | MBE | RMSE
[8 empty] | 8 | Tamb | ASTM | -0.01 | 1.17 | <- Mono baseline
Method 1 results with site-measured albedo and GHI/DHI field measurements | [7 empty] | 8 | Tmod | ASTM | 0.68 | 1.65
SAMS02 DHI+GHI Perez | [7 empty] | 2+4 | POA | ASTM | 0.24 | 1.81 | <- Method 1
[8 empty] | 2+4 | Gtotal | ASTM | -1.3 | 1.16 | <- Method 2
Row | Method | ASTM / IEC | MBE | RMSE | MAX | MIN |  | 2+4 | Method4 | ASTM | -0.33 | 0.85 | <- Method 4
8 | Tamb | ASTM | 0 | 1.13 | 1.034 | 0.9805 | <- Mono baseline | 2+4 | Method4Min | ASTM | 1.08 | 1.44 | <- Method 4_min
2+4 | POA | ASTM | 0.57 | 1.5 | 1.0631 | 0.9826 | <- Method 1
SAMP07 (CM11 POA and high freq albedo) - row 2+4
[8 empty] | Row | Method | ASTM / IEC | MBE | RMSE
[8 empty] | 8 | Tamb | ASTM | 0.01 | 1.76 | <- Mono baseline
[8 empty] | 8 | Tmod | ASTM | 0.9 | 1.99
[8 empty] | 2+4 | POA | ASTM | 0.43 | 2.84 | <- Method 1
[8 empty] | 2+4 | Gtotal | ASTM | -1.33 | 1.6 | <- Method 2
[8 empty] | 2+4 | Method4 | ASTM | -0.58 | 0.93 | <- Method 4
[8 empty] | 2+4 | Method4Min | ASTM | 1.03 | 1.83 | <- Method 4_min |  |  | Method4_calibration_3_29_2023.ipynb
SAMP00 (RefCell POA, high frequency albedo)
[8 empty] | Row | Method | ASTM / IEC | MBE | RMSE
[8 empty] | 8 | Tamb | ASTM | 0 | 1.68 | <- Mono baseline
[8 empty] | 8 | Tmod | ASTM | 0.91 | 1.88
[8 empty] | 2+4 | POA | ASTM | 0.46 | 2.49 | <- Method 1
[8 empty] | 2+4 | Gtotal | ASTM | -1.31 | 1.66 | <- Method 2
[8 empty] | 2+4 | Method4 | ASTM | -0.57 | 1.26 | <- Method 4
ROW 2+4 TMY2020
ROW 2+4 SAM_P07

## model_error
|  | monofacial | bifacial_baseline | method2
2021-06-07 | 17:00:00-07:00 | 1.5177 | 0.62634 | 1.1612
2021-06-14 | 10:00:00-07:00 | 1.6077 | 0.51526 | 1.3343
2021-06-21 | 03:15:00-07:00 | 1.0558 | 0.75105 | 1.1175
2021-06-29 | 17:45:00-07:00 | 1.4564 | 0.7558 | 1.4744
2021-07-07 | 14:30:00-07:00 | 1.6937 | 0.72352 | 1.3926
2021-07-14 | 07:30:00-07:00 | 1.5317 | 0.61673 | 1.147
2021-07-21 | 00:30:00-07:00 | 1.6829 | 1.0191 | 1.2634
2021-07-28 | 13:30:00-07:00 | 1.3477 | 0.91066 | 1.1918
2021-08-04 | 06:45:00-07:00 | 1.7212 | 1.0113 | 1.5711
2021-08-10 | 23:45:00-07:00 | 1.4562 | 0.90059 | 1.3393
2021-08-17 | 16:45:00-07:00 | 1.1996 | 0.57405 | 1.1582
2021-08-24 | 13:30:00-07:00 | 1.1849 | 0.67772 | 0.99182
2021-08-31 | 06:30:00-07:00 | 1.6443 | 0.79749 | 1.1888
2021-09-06 | 23:30:00-07:00 | 0.96418 | 0.5177 | 0.99069
2021-09-13 | 17:00:00-07:00 | 1.4748 | 0.77347 | 1.3972
2021-09-20 | 10:00:00-07:00 | 1.9952 | 1.6554 | 1.8298
2021-09-28 | 01:30:00-07:00 | 1.8323 | 0.86203 | 1.4981
2021-10-04 | 18:30:00-07:00 | 1.2154 | 0.74226 | 1.0887
2021-10-11 | 11:30:00-07:00 | 1.5799 | 0.63411 | 1.4423
2021-10-18 | 04:30:00-07:00 | 1.0752 | 0.60709 | 1.0041
2021-10-27 | 16:30:00-07:00 | 1.2125 | 0.74618 | 1.2066
2021-11-03 | 09:30:00-07:00 | 0.92364 | 0.7477 | 0.84271
2021-11-10 | 02:30:00-07:00 | 0.84155 | 0.93064 | 0.70538
2021-11-16 | 19:30:00-07:00 | 0.56447 | 0.94738 | 0.76095
2021-11-23 | 13:00:00-07:00 | 0.73906 | 5.7335 | 0.75925
2021-11-30 | 06:00:00-07:00 | 0.73997 | 2.29 | 0.61833
2021-12-06 | 23:15:00-07:00 | 0.77126 | 1.5093 | 0.56446
2021-12-13 | 16:15:00-07:00 | 0.55825 | 5.1886 | 0.52267
2021-12-20 | 09:15:00-07:00 | 0.49893 | 1.5318 | 0.40462
2021-12-27 | 02:45:00-07:00 | 0.52426 | 0.5531 | 0.41177
2022-01-02 | 19:45:00-07:00 | 0.42023 | 3.6064 | 0.55425
2022-01-09 | 13:00:00-07:00 | 0.84206 | 4.9416 | 1.7191
2022-01-16 | 06:00:00-07:00 | 0.42103 | 1.1705 | 0.52452
2022-01-22 | 23:00:00-07:00 | 0.57831 | 0.85366 | 0.6244
2022-01-29 | 16:00:00-07:00 | 0.7908 | 1.4729 | 1.0141
2022-02-05 | 09:00:00-07:00 | 0.57915 | 0.86003 | 0.60845
2022-02-12 | 02:00:00-07:00 | 0.76029 | 0.78133 | 0.70292
2022-02-18 | 19:30:00-07:00 | 0.92474 | 2.4834 | 0.88345
2022-02-28 | 08:45:00-07:00 | 1.3062 | 1.6416 | 1.274
2022-03-08 | 16:00:00-07:00 | 0.94251 | 2.553 | 0.70014
2022-03-16 | 19:15:00-07:00 | 1.1352 | 5.2866 | 0.9514
2022-03-23 | 12:15:00-07:00 | 1.0186 | 0.92873 | 1.0136
2022-03-30 | 05:15:00-07:00 | 1.0474 | 0.60912 | 1.2124
2022-04-05 | 22:30:00-07:00 | 1.1579 | 0.92661 | 1.2591
2022-04-15 | 00:15:00-07:00 | 1.0384 | 0.85759 | 1.1372
2022-04-21 | 17:15:00-07:00 | 1.8063 | 1.053 | 1.349
2022-04-28 | 10:30:00-07:00 | 2.0041 | 4.7474 | 1.7073
2022-05-05 | 03:30:00-07:00 | 1.5986 | 0.7893 | 1.1423
2022-05-11 | 20:30:00-07:00 | 1.6812 | 0.81656 | 1.5069
2022-05-18 | 13:45:00-07:00 | 1.2863 | 5.1215 | 1.1346
2022-05-25 | 07:15:00-07:00 | 1.1589 | 0.95369 | 1.2939

## SAM_TMY2020_row8
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio | Albedo_actual
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70434 | 0.71297 | 0.014518 | 1.0122 | 815.377 | 24.6902 | 2.5534 | 1.1062 | 0.20104
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.70617 | 0.7062 | 0.014732 | 1 | 815.377 | 24.6902 | 2.5534 | 1.0064 | 0.21465
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.70694 | 0.69344 | 0.010248 | 0.98091 | 815.377 | 24.6902 | 2.5534 | 0.91649 | 0.20108
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70669 | 0.70161 | 0.014994 | 0.99281 | 815.377 | 24.6902 | 2.5534 | 1.1044 | 0.18924
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.68433 | 0.67739 | 0.016735 | 0.98986 | 790.957 | 26.7545 | 2.4147 | 1.0617 | 0.20199
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.68144 | 0.67914 | 0.015025 | 0.99663 | 790.957 | 26.7545 | 2.4147 | 0.9922 | 0.19409
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.68293 | 0.66349 | 0.018728 | 0.97153 | 790.957 | 26.7545 | 2.4147 | 1.1624 | 0.19023
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.68287 | 0.66911 | 0.013027 | 0.97985 | 790.957 | 26.7545 | 2.4147 | 1.0223 | 0.18185
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.58702 | 0.58343 | 0.016668 | 0.99389 | 669.655 | 25.4276 | 2.3727 | 1.0985 | 0.18577
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.58228 | 0.58557 | 0.014935 | 1.0057 | 669.655 | 25.4276 | 2.3727 | 1.1618 | 0.18466
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.58339 | 0.58655 | 0.011753 | 1.0054 | 669.655 | 25.4276 | 2.3727 | 1.14 | 0.17984
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.58639 | 0.58857 | 0.011675 | 1.0037 | 669.655 | 25.4276 | 2.3727 | 1.1966 | 0.20006
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.58468 | 0.57709 | 0.017043 | 0.98702 | 669.655 | 25.4276 | 2.3727 | 1.1745 | 0.21052
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.64586 | 0.62911 | 0.0099971 | 0.97408 | 720.547 | 20.9691 | 2.4432 | 1.1121 | 0.21541
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.64659 | 0.62762 | 0.014119 | 0.97066 | 720.547 | 20.9691 | 2.4432 | 0.96336 | 0.22237
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.6402 | 0.64176 | 0.019262 | 1.0024 | 720.547 | 20.9691 | 2.4432 | 1.276 | 0.21775
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.64135 | 0.63772 | 0.020594 | 0.99434 | 720.547 | 20.9691 | 2.4432 | 0.9354 | 0.21258
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.56966 | 0.56157 | 0.01306 | 0.98581 | 611.291 | 14.2291 | 2.7405 | 1.1945 | 0.2226
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.56776 | 0.56915 | 0.014471 | 1.0025 | 611.291 | 14.2291 | 2.7405 | 1.0724 | 0.22062
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.56942 | 0.5709 | 0.010647 | 1.0026 | 611.291 | 14.2291 | 2.7405 | 1.11 | 0.22259
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.57118 | 0.56716 | 0.013559 | 0.99296 | 611.291 | 14.2291 | 2.7405 | 0.97089 | 0.22689
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.48866 | 0.4825 | 0.0094922 | 0.98741 | 513.208 | 8.4866 | 2.5476 | 0.98877 | 0.22736
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.491 | 0.49384 | 0.0089041 | 1.0058 | 513.208 | 8.4866 | 2.5476 | 1.1413 | 0.22352
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.49391 | 0.48942 | 0.0050927 | 0.99091 | 513.208 | 8.4866 | 2.5476 | 1.1315 | 0.24139
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.4908 | 0.494 | 0.0078651 | 1.0065 | 513.208 | 8.4866 | 2.5476 | 0.99471 | 0.26171
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.49486 | 0.49311 | 0.0073566 | 0.99646 | 513.208 | 8.4866 | 2.5476 | 1.1644 | 0.23359
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.41575 | 0.41702 | 0.0071756 | 1.0031 | 421.538 | 3.3412 | 3.1782 | 1.1084 | 0.29322
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.41469 | 0.41611 | 0.0054051 | 1.0034 | 421.538 | 3.3412 | 3.1782 | 1.2695 | 0.2338
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.41512 | 0.41804 | 0.0045589 | 1.007 | 421.538 | 3.3412 | 3.1782 | 1.1765 | 0.24579
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.41446 | 0.4184 | 0.0051556 | 1.0095 | 421.538 | 3.3412 | 3.1782 | 1.1678 | 0.44009
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.42189 | 0.4211 | 0.0042157 | 0.99812 | 428.325 | 2.1398 | 2.3806 | 1.1643 | 0.60833
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.41846 | 0.42474 | 0.0083584 | 1.015 | 428.325 | 2.1398 | 2.3806 | 1.0223 | 0.32067
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.42298 | 0.41406 | 0.0040214 | 0.97891 | 428.325 | 2.1398 | 2.3806 | 0.96075 | 0.26609
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.41985 | 0.42433 | 0.0053797 | 1.0107 | 428.325 | 2.1398 | 2.3806 | 1.6316 | 0.63986
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.41903 | 0.41367 | 0.0077315 | 0.9872 | 428.325 | 2.1398 | 2.3806 | 1.2878 | 0.64239
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.50952 | 0.50799 | 0.0057752 | 0.99699 | 519.153 | 3.06 | 3.1041 | 1.3707 | 0.39554
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.50348 | 0.51197 | 0.0076525 | 1.0169 | 519.153 | 3.06 | 3.1041 | 1.3686 | 0.3917
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.50387 | 0.51022 | 0.0091823 | 1.0126 | 519.153 | 3.06 | 3.1041 | 1.0647 | 0.39736
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.50778 | 0.51639 | 0.01341 | 1.017 | 519.153 | 3.06 | 3.1041 | 1.3493 | 0.42006
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.6026 | 0.60336 | 0.0087986 | 1.0013 | 630.886 | 5.2134 | 3.0028 | 1.0803 | 0.36541
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.59955 | 0.61167 | 0.010867 | 1.0202 | 630.886 | 5.2134 | 3.0028 | 1.1412 | 0.39193
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.59945 | 0.60848 | 0.010492 | 1.0151 | 630.886 | 5.2134 | 3.0028 | 0.96151 | 0.16776
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.60359 | 0.59478 | 0.010787 | 0.98539 | 630.886 | 5.2134 | 3.0028 | 1.0102 | 0.17874
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.57289 | 0.57436 | 0.01202 | 1.0026 | 606.561 | 9.9782 | 3.4138 | 1.0913 | 0.18798
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.57171 | 0.57676 | 0.010731 | 1.0088 | 606.561 | 9.9782 | 3.4138 | 1.1396 | 0.19201
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.5714 | 0.5832 | 0.018231 | 1.0206 | 606.561 | 9.9782 | 3.4138 | 1.2531 | 0.1907
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.57315 | 0.56784 | 0.021376 | 0.99075 | 606.561 | 9.9782 | 3.4138 | 0.95894 | 0.18178
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.59469 | 0.59457 | 0.014891 | 0.9998 | 648.471 | 14.253 | 2.8131 | 1.0667 | 0.18184
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.59757 | 0.60775 | 0.016861 | 1.017 | 648.471 | 14.253 | 2.8131 | 1.3256 | 0.18693
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.58936 | 0.59969 | 0.013222 | 1.0175 | 648.471 | 14.253 | 2.8131 | 1.1728 | 0.2797
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.59227 | 0.60775 | 0.012063 | 1.0261 | 648.471 | 14.253 | 2.8131 | 1.103 | 0.18455
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_TMY2020_row24_POA
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.73932 | 0.74147 | 0.0063251 | 1.0029 | 815.377 | 24.6902 | 2.5534 | 1.09
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.73897 | 0.73882 | 0.0051594 | 0.99979 | 815.377 | 24.6902 | 2.5534 | 0.99627
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.73945 | 0.73944 | 0.0070782 | 0.99998 | 815.377 | 24.6902 | 2.5534 | 0.90011
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.74015 | 0.74536 | 0.0068617 | 1.007 | 815.377 | 24.6902 | 2.5534 | 1.1046
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.71333 | 0.71167 | 0.0069734 | 0.99769 | 790.957 | 26.7545 | 2.4147 | 1.0484
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.71078 | 0.72103 | 0.0061016 | 1.0144 | 790.957 | 26.7545 | 2.4147 | 0.98441
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.71066 | 0.70343 | 0.010689 | 0.98982 | 790.957 | 26.7545 | 2.4147 | 1.0726
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.71076 | 0.71114 | 0.0087849 | 1.0005 | 790.957 | 26.7545 | 2.4147 | 0.99246
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.61825 | 0.62837 | 0.010082 | 1.0164 | 669.655 | 25.4276 | 2.3727 | 1.0108
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.61703 | 0.61746 | 0.0086569 | 1.0007 | 669.655 | 25.4276 | 2.3727 | 1.1071
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.61925 | 0.61899 | 0.005912 | 0.99959 | 669.655 | 25.4276 | 2.3727 | 1.0684
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.61929 | 0.61472 | 0.0070526 | 0.99261 | 669.655 | 25.4276 | 2.3727 | 1.1834
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.61856 | 0.61604 | 0.0074031 | 0.99593 | 669.655 | 25.4276 | 2.3727 | 1.0546
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.67346 | 0.66147 | 0.0048647 | 0.9822 | 720.547 | 20.9691 | 2.4432 | 1.0682
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.6715 | 0.66894 | 0.0076318 | 0.99618 | 720.547 | 20.9691 | 2.4432 | 0.97663
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.67383 | 0.68229 | 0.017565 | 1.0126 | 720.547 | 20.9691 | 2.4432 | 1.2396
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.67566 | 0.68458 | 0.0082053 | 1.0132 | 720.547 | 20.9691 | 2.4432 | 0.93962
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.59596 | 0.59738 | 0.0075678 | 1.0024 | 611.291 | 14.2291 | 2.7405 | 1.0988
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.59939 | 0.60726 | 0.0062865 | 1.0131 | 611.291 | 14.2291 | 2.7405 | 1.005
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.59758 | 0.61695 | 0.0063675 | 1.0324 | 611.291 | 14.2291 | 2.7405 | 1.0677
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.59566 | 0.60821 | 0.0075786 | 1.0211 | 611.291 | 14.2291 | 2.7405 | 1.0254
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.51103 | 0.52568 | 0.0072707 | 1.0287 | 513.208 | 8.4866 | 2.5476 | 0.94944
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.51379 | 0.5324 | 0.0083731 | 1.0362 | 513.208 | 8.4866 | 2.5476 | 1.1193
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.52286 | 0.53272 | 0.0095872 | 1.0189 | 513.208 | 8.4866 | 2.5476 | 1.2149
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.52684 | 0.52843 | 0.060865 | 1.003 | 513.208 | 8.4866 | 2.5476 | 0.92044
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.52466 | 0.52558 | 0.023159 | 1.0018 | 513.208 | 8.4866 | 2.5476 | 1.0648
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.43928 | 0.45468 | 0.014948 | 1.035 | 421.538 | 3.3412 | 3.1782 | 1.1129
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.47768 | 0.45195 | 0.051675 | 0.94613 | 421.538 | 3.3412 | 3.1782 | 1.1442
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.44155 | 0.45042 | 0.015167 | 1.0201 | 421.538 | 3.3412 | 3.1782 | 1.1829
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.43929 | 0.45292 | 0.0051784 | 1.031 | 421.538 | 3.3412 | 3.1782 | 1.086
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.45429 | 0.49638 | 0.034852 | 1.0926 | 428.325 | 2.1398 | 2.3806 | 0.96655
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.44933 | 0.48042 | 0.050643 | 1.0692 | 428.325 | 2.1398 | 2.3806 | 0.8963
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.44109 | 0.45914 | 0.012077 | 1.0409 | 428.325 | 2.1398 | 2.3806 | 1.0224
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.44646 | 0.44161 | 0.0091058 | 0.98914 | 428.325 | 2.1398 | 2.3806 | 1.6148
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.44537 | 0.46643 | 0.014899 | 1.0473 | 428.325 | 2.1398 | 2.3806 | 1.2361
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.53362 | 0.56955 | 0.008704 | 1.0673 | 519.153 | 3.06 | 3.1041 | 1.2715
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.53386 | 0.54969 | 0.0080531 | 1.0297 | 519.153 | 3.06 | 3.1041 | 1.202
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.54127 | 0.55378 | 0.023644 | 1.0231 | 519.153 | 3.06 | 3.1041 | 1.1212
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.53143 | 0.54504 | 0.015489 | 1.0256 | 519.153 | 3.06 | 3.1041 | 1.0977
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.6687 | 0.67043 | 0.025371 | 1.0026 | 630.886 | 5.2134 | 3.0028 | 1.0498
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.69483 | 0.66071 | 0.053221 | 0.95089 | 630.886 | 5.2134 | 3.0028 | 1.063
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.63746 | 0.65135 | 0.0096262 | 1.0218 | 630.886 | 5.2134 | 3.0028 | 1.044
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.63384 | 0.64145 | 0.0060251 | 1.012 | 630.886 | 5.2134 | 3.0028 | 0.92305
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.60193 | 0.60833 | 0.0089842 | 1.0106 | 606.561 | 9.9782 | 3.4138 | 1.0144
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.60244 | 0.61357 | 0.0091576 | 1.0185 | 606.561 | 9.9782 | 3.4138 | 1.0063
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.60521 | 0.61203 | 0.010206 | 1.0113 | 606.561 | 9.9782 | 3.4138 | 1.1121
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.62724 | 0.60937 | 0.048723 | 0.9715 | 606.561 | 9.9782 | 3.4138 | 0.89591
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.62887 | 0.64097 | 0.0075403 | 1.0192 | 648.471 | 14.253 | 2.8131 | 1.03
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.62994 | 0.63355 | 0.0075371 | 1.0057 | 648.471 | 14.253 | 2.8131 | 1.0912
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.65687 | 0.64351 | 0.052077 | 0.97965 | 648.471 | 14.253 | 2.8131 | 1.1392
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.62833 | 0.65405 | 0.0092238 | 1.0409 | 648.471 | 14.253 | 2.8131 | 1.0031
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_TMY2020_row24_Gtotal
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70413 | 0.69749 | 0.01268 | 0.99057 | 799.5404 | 24.37 | 2.5945 | 1.1171
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.70461 | 0.69215 | 0.013379 | 0.98232 | 799.5404 | 24.37 | 2.5945 | 1.0331
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.70441 | 0.68666 | 0.010871 | 0.9748 | 799.5404 | 24.37 | 2.5945 | 0.9027
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70642 | 0.69236 | 0.014925 | 0.98011 | 799.5404 | 24.37 | 2.5945 | 1.113
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.72219 | 0.70171 | 0.014109 | 0.97164 | 827.5098 | 26.6795 | 2.4095 | 1.0849
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.72034 | 0.70551 | 0.010975 | 0.97942 | 827.5098 | 26.6795 | 2.4095 | 1.0175
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.72318 | 0.69324 | 0.012439 | 0.9586 | 827.5098 | 26.6795 | 2.4095 | 1.1268
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.71987 | 0.69695 | 0.012167 | 0.96815 | 827.5098 | 26.6795 | 2.4095 | 1.0131
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.61922 | 0.60723 | 0.015646 | 0.98062 | 693.4789 | 25.0822 | 2.3786 | 1.0772
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.61533 | 0.60364 | 0.013497 | 0.98099 | 693.4789 | 25.0822 | 2.3786 | 1.1364
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.61587 | 0.60437 | 0.011223 | 0.98132 | 693.4789 | 25.0822 | 2.3786 | 1.1187
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.61891 | 0.60478 | 0.0093112 | 0.97716 | 693.4789 | 25.0822 | 2.3786 | 1.1032
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.61746 | 0.59702 | 0.013065 | 0.9669 | 693.4789 | 25.0822 | 2.3786 | 1.1867
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.68663 | 0.65383 | 0.009739 | 0.95223 | 758.3519 | 21.0153 | 2.4291 | 1.1032
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.68688 | 0.65586 | 0.014065 | 0.95485 | 758.3519 | 21.0153 | 2.4291 | 0.96362
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.68137 | 0.67027 | 0.017592 | 0.98371 | 758.3519 | 21.0153 | 2.4291 | 1.3022
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.68176 | 0.67003 | 0.014889 | 0.9828 | 758.3519 | 21.0153 | 2.4291 | 0.95504
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.60442 | 0.58309 | 0.011768 | 0.96471 | 637.317 | 14.1509 | 2.7565 | 1.2146
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.60142 | 0.59407 | 0.013512 | 0.98778 | 637.317 | 14.1509 | 2.7565 | 1.0904
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.60393 | 0.59633 | 0.0099046 | 0.98743 | 637.317 | 14.1509 | 2.7565 | 1.1044
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.60514 | 0.59585 | 0.011718 | 0.98465 | 637.317 | 14.1509 | 2.7565 | 0.97709
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.54915 | 0.54104 | 0.0094684 | 0.98523 | 566.4177 | 8.3115 | 2.576 | 0.97652
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.55667 | 0.546 | 0.007145 | 0.98083 | 566.4177 | 8.3115 | 2.576 | 1.1462
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.55644 | 0.54297 | 0.0072915 | 0.97579 | 566.4177 | 8.3115 | 2.576 | 1.1861
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.55238 | 0.54372 | 0.0071926 | 0.98432 | 566.4177 | 8.3115 | 2.576 | 0.91682
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.55497 | 0.54413 | 0.0062729 | 0.98047 | 566.4177 | 8.3115 | 2.576 | 1.1093
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.43307 | 0.42851 | 0.0054978 | 0.98947 | 432.218 | 3.5632 | 3.0885 | 1.04
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.43154 | 0.42713 | 0.0052382 | 0.98979 | 432.218 | 3.5632 | 3.0885 | 1.0851
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.43244 | 0.42932 | 0.0041556 | 0.99279 | 432.218 | 3.5632 | 3.0885 | 1.1216
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.43235 | 0.43353 | 0.0039032 | 1.0027 | 432.218 | 3.5632 | 3.0885 | 1.1117
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.44008 | 0.42857 | 0.0056484 | 0.97384 | 440.6495 | 2.0312 | 2.3745 | 1.1239
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.4392 | 0.42787 | 0.015857 | 0.9742 | 440.6495 | 2.0312 | 2.3745 | 0.87093
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.44146 | 0.4315 | 0.0050214 | 0.97744 | 440.6495 | 2.0312 | 2.3745 | 0.96075
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.44045 | 0.43563 | 0.0061501 | 0.98906 | 440.6495 | 2.0312 | 2.3745 | 1.4382
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.43968 | 0.4312 | 0.0096581 | 0.98072 | 440.6495 | 2.0312 | 2.3745 | 1.1568
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.54889 | 0.54348 | 0.0063253 | 0.99015 | 550.8517 | 3.0463 | 3.0887 | 1.2676
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.54412 | 0.53445 | 0.0066445 | 0.98225 | 550.8517 | 3.0463 | 3.0887 | 1.2311
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.54298 | 0.54311 | 0.0086661 | 1.0002 | 550.8517 | 3.0463 | 3.0887 | 0.88582
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.54599 | 0.5392 | 0.01254 | 0.98756 | 550.8517 | 3.0463 | 3.0887 | 1.2256
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.67036 | 0.65648 | 0.00749 | 0.9793 | 695.2192 | 5.293 | 2.9426 | 0.97508
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.66786 | 0.67322 | 0.0094979 | 1.008 | 695.2192 | 5.293 | 2.9426 | 1.069
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.66602 | 0.6721 | 0.01001 | 1.0091 | 695.2192 | 5.293 | 2.9426 | 1.0158
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.67576 | 0.66198 | 0.012156 | 0.9796 | 695.2192 | 5.293 | 2.9426 | 1.0592
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.62398 | 0.62156 | 0.012266 | 0.99611 | 655.3085 | 10.1107 | 3.3939 | 1.0914
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.62434 | 0.62434 | 0.011284 | 0.99999 | 655.3085 | 10.1107 | 3.3939 | 1.0886
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.62679 | 0.62859 | 0.013286 | 1.0029 | 655.3085 | 10.1107 | 3.3939 | 1.0549
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.62915 | 0.62192 | 0.017533 | 0.98851 | 655.3085 | 10.1107 | 3.3939 | 0.89526
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.63578 | 0.63567 | 0.011905 | 0.99984 | 683.2209 | 14.2326 | 2.8166 | 0.95284
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.63742 | 0.63341 | 0.014068 | 0.99371 | 683.2209 | 14.2326 | 2.8166 | 1.2487
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.63099 | 0.6289 | 0.01112 | 0.99668 | 683.2209 | 14.2326 | 2.8166 | 1.1093
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.63415 | 0.64048 | 0.012288 | 1.01 | 683.2209 | 14.2326 | 2.8166 | 1.0659
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_TMY2020_row24_Method4
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70413 | 0.70836 | 0.012005 | 1.006 | 799.5404 | 24.37 | 2.5945
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.70461 | 0.70845 | 0.013179 | 1.0055 | 799.5404 | 24.37 | 2.5945
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.70441 | 0.70046 | 0.010614 | 0.9944 | 799.5404 | 24.37 | 2.5945
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70642 | 0.69456 | 0.014134 | 0.98322 | 799.5404 | 24.37 | 2.5945
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.72219 | 0.71385 | 0.014027 | 0.98845 | 827.5098 | 26.6795 | 2.4095
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.72034 | 0.71498 | 0.010936 | 0.99256 | 827.5098 | 26.6795 | 2.4095
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.72318 | 0.71007 | 0.013123 | 0.98188 | 827.5098 | 26.6795 | 2.4095
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.71987 | 0.71044 | 0.012277 | 0.9869 | 827.5098 | 26.6795 | 2.4095
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.61922 | 0.61596 | 0.015163 | 0.99472 | 693.4789 | 25.0822 | 2.3786
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.61533 | 0.61672 | 0.013223 | 1.0023 | 693.4789 | 25.0822 | 2.3786
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.61587 | 0.61651 | 0.011706 | 1.001 | 693.4789 | 25.0822 | 2.3786
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.61891 | 0.61504 | 0.010147 | 0.99374 | 693.4789 | 25.0822 | 2.3786
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.61746 | 0.6103 | 0.012237 | 0.98841 | 693.4789 | 25.0822 | 2.3786
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.68663 | 0.67255 | 0.0098752 | 0.97949 | 758.3519 | 21.0153 | 2.4291
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.68688 | 0.67207 | 0.013605 | 0.97845 | 758.3519 | 21.0153 | 2.4291
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.68137 | 0.67737 | 0.019262 | 0.99414 | 758.3519 | 21.0153 | 2.4291
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.68176 | 0.67694 | 0.015107 | 0.99293 | 758.3519 | 21.0153 | 2.4291
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.60442 | 0.59115 | 0.010584 | 0.97804 | 637.317 | 14.1509 | 2.7565
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.60142 | 0.59934 | 0.014576 | 0.99655 | 637.317 | 14.1509 | 2.7565
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.60393 | 0.59833 | 0.0096279 | 0.99074 | 637.317 | 14.1509 | 2.7565
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.60514 | 0.6013 | 0.011808 | 0.99365 | 637.317 | 14.1509 | 2.7565
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.54915 | 0.53994 | 0.0090494 | 0.98323 | 566.4177 | 8.3115 | 2.576
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.55667 | 0.54815 | 0.0070754 | 0.9847 | 566.4177 | 8.3115 | 2.576
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.55644 | 0.54579 | 0.0072566 | 0.98086 | 566.4177 | 8.3115 | 2.576
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.55238 | 0.54388 | 0.0072661 | 0.9846 | 566.4177 | 8.3115 | 2.576
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.55497 | 0.54399 | 0.0060655 | 0.98022 | 566.4177 | 8.3115 | 2.576
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.43307 | 0.42631 | 0.0062369 | 0.98439 | 432.218 | 3.5632 | 3.0885
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.43154 | 0.42621 | 0.0048426 | 0.98766 | 432.218 | 3.5632 | 3.0885
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.43244 | 0.42746 | 0.0039571 | 0.9885 | 432.218 | 3.5632 | 3.0885
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.43235 | 0.42726 | 0.0039583 | 0.98823 | 432.218 | 3.5632 | 3.0885
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.44008 | 0.43385 | 0.0054627 | 0.98584 | 440.6495 | 2.0312 | 2.3745
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.4392 | 0.43463 | 0.016074 | 0.98959 | 440.6495 | 2.0312 | 2.3745
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.44146 | 0.43638 | 0.0051335 | 0.98849 | 440.6495 | 2.0312 | 2.3745
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.44045 | 0.43659 | 0.00621 | 0.99123 | 440.6495 | 2.0312 | 2.3745
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.43926 | 0.42833 | 0.010144 | 0.97512 | 440.6495 | 2.0312 | 2.3745
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.54889 | 0.54225 | 0.0062703 | 0.98791 | 550.8517 | 3.0463 | 3.0887
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.54412 | 0.54246 | 0.0068894 | 0.99695 | 550.8517 | 3.0463 | 3.0887
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.54298 | 0.54696 | 0.0087678 | 1.0073 | 550.8517 | 3.0463 | 3.0887
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.54599 | 0.54812 | 0.01254 | 1.0039 | 550.8517 | 3.0463 | 3.0887
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.67036 | 0.66488 | 0.008094 | 0.99183 | 695.2192 | 5.293 | 2.9426
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.66786 | 0.66905 | 0.0093731 | 1.0018 | 695.2192 | 5.293 | 2.9426
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.66602 | 0.67939 | 0.009756 | 1.0201 | 695.2192 | 5.293 | 2.9426
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.67576 | 0.66506 | 0.012129 | 0.98416 | 695.2192 | 5.293 | 2.9426
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.62398 | 0.62219 | 0.012675 | 0.99714 | 655.3085 | 10.1107 | 3.3939
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.62434 | 0.62433 | 0.010367 | 0.99998 | 655.3085 | 10.1107 | 3.3939
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.62679 | 0.62681 | 0.013157 | 1 | 655.3085 | 10.1107 | 3.3939
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.62915 | 0.62044 | 0.017608 | 0.98617 | 655.3085 | 10.1107 | 3.3939
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.63578 | 0.63577 | 0.012076 | 1 | 683.2209 | 14.2326 | 2.8166
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.63742 | 0.639 | 0.015537 | 1.0025 | 683.2209 | 14.2326 | 2.8166
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.63099 | 0.63029 | 0.011326 | 0.99889 | 683.2209 | 14.2326 | 2.8166
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.63415 | 0.63231 | 0.012896 | 0.99709 | 683.2209 | 14.2326 | 2.8166
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_TMYA01_POA
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.74916 | 0.74808 | 0.0070985 | 0.99856 | 824.628 | 24.7768 | 2.5208 | 1.0808
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.75154 | 0.74554 | 0.0052893 | 0.99202 | 824.628 | 24.7768 | 2.5208 | 0.97988
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.75207 | 0.74638 | 0.0078281 | 0.99244 | 824.628 | 24.7768 | 2.5208 | 0.89527
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.75028 | 0.75181 | 0.0070699 | 1.002 | 824.628 | 24.7768 | 2.5208 | 1.0765
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.71669 | 0.71251 | 0.0067542 | 0.99417 | 792.077 | 26.791 | 2.4155 | 1.036
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.71598 | 0.72192 | 0.0066073 | 1.0083 | 792.077 | 26.791 | 2.4155 | 0.96595
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.71615 | 0.70429 | 0.011008 | 0.98343 | 792.077 | 26.791 | 2.4155 | 1.0612
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.71467 | 0.71199 | 0.0088464 | 0.99624 | 792.077 | 26.791 | 2.4155 | 0.98129
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.62183 | 0.62955 | 0.012724 | 1.0124 | 671.098 | 25.4276 | 2.3727 | 1.0007
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.62013 | 0.61861 | 0.010049 | 0.99754 | 671.098 | 25.4276 | 2.3727 | 1.0948
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.62193 | 0.62017 | 0.0064368 | 0.99718 | 671.098 | 25.4276 | 2.3727 | 1.0662
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.6236 | 0.61597 | 0.0080478 | 0.98777 | 671.098 | 25.4276 | 2.3727 | 1.178
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.62441 | 0.61702 | 0.0093493 | 0.98817 | 671.098 | 25.4276 | 2.3727 | 1.0567
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.67301 | 0.65696 | 0.0064826 | 0.97615 | 715.047 | 20.8755 | 2.421 | 1.0555
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.66985 | 0.66444 | 0.0080154 | 0.99191 | 715.047 | 20.8755 | 2.421 | 0.93994
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.67504 | 0.67769 | 0.02005 | 1.0039 | 715.047 | 20.8755 | 2.421 | 1.2218
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.67604 | 0.68002 | 0.0095358 | 1.0059 | 715.047 | 20.8755 | 2.421 | 0.9303
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.5997 | 0.59619 | 0.0095752 | 0.99416 | 609.856 | 14.1965 | 2.745 | 1.1292
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.60564 | 0.60607 | 0.013058 | 1.0007 | 609.856 | 14.1965 | 2.745 | 1.0084
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.60374 | 0.61579 | 0.011249 | 1.02 | 609.856 | 14.1965 | 2.745 | 1.0636
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.60114 | 0.60694 | 0.013289 | 1.0096 | 609.856 | 14.1965 | 2.745 | 0.99566
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.50088 | 0.51547 | 0.012305 | 1.0291 | 502.057 | 8.5 | 2.5532 | 0.92029
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.5082 | 0.52201 | 0.013027 | 1.0272 | 502.057 | 8.5 | 2.5532 | 1.07
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.51915 | 0.52204 | 0.011385 | 1.0056 | 502.057 | 8.5 | 2.5532 | 1.1407
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.52426 | 0.51987 | 0.018052 | 0.99163 | 502.057 | 8.5 | 2.5532 | 1.0073
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.52003 | 0.51512 | 0.015479 | 0.99054 | 502.057 | 8.5 | 2.5532 | 1.0635
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.44767 | 0.45621 | 0.014964 | 1.0191 | 422.989 | 3.4327 | 3.1439 | 1.091
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.44606 | 0.45324 | 0.025852 | 1.0161 | 422.989 | 3.4327 | 3.1439 | 1.1105
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.4397 | 0.45175 | 0.014663 | 1.0274 | 422.989 | 3.4327 | 3.1439 | 1.0982
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.44361 | 0.45421 | 0.014956 | 1.0239 | 422.989 | 3.4327 | 3.1439 | 1.095
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.45558 | 0.49884 | 0.02433 | 1.095 | 430.677 | 2.2391 | 2.3696 | 1.2049
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.45035 | 0.48205 | 0.054271 | 1.0704 | 430.677 | 2.2391 | 2.3696 | 0.84875
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.4473 | 0.46167 | 0.012769 | 1.0321 | 430.677 | 2.2391 | 2.3696 | 1.043
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.46208 | 0.44398 | 0.028011 | 0.96081 | 430.677 | 2.2391 | 2.3696 | 1.657
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.45221 | 0.46851 | 0.046443 | 1.036 | 430.677 | 2.2391 | 2.3696 | 1.3628
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.56632 | 0.588 | 0.056988 | 1.0383 | 535.699 | 2.9492 | 3.0928 | 1.3162
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.55288 | 0.56588 | 0.016818 | 1.0235 | 535.699 | 2.9492 | 3.0928 | 1.2192
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.56817 | 0.57426 | 0.017275 | 1.0107 | 535.699 | 2.9492 | 3.0928 | 0.96846
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.54864 | 0.56567 | 0.020422 | 1.031 | 535.699 | 2.9492 | 3.0928 | 1.0529
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.71205 | 0.67981 | 0.050351 | 0.95472 | 644.341 | 5.2231 | 2.9924 | 1.0007
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.65997 | 0.67385 | 0.016527 | 1.021 | 644.341 | 5.2231 | 2.9924 | 1.178
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.64522 | 0.66331 | 0.0080922 | 1.028 | 644.341 | 5.2231 | 2.9924 | 1.0618
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.64638 | 0.65306 | 0.0052192 | 1.0103 | 644.341 | 5.2231 | 2.9924 | 1.0024
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.59931 | 0.60141 | 0.0087993 | 1.0035 | 598.574 | 9.9307 | 3.4175 | 0.99719
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.59746 | 0.60699 | 0.0073181 | 1.0159 | 598.574 | 9.9307 | 3.4175 | 0.98644
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.59877 | 0.60479 | 0.0098024 | 1.01 | 598.574 | 9.9307 | 3.4175 | 1.0233
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.60184 | 0.60217 | 0.0086799 | 1.0005 | 598.574 | 9.9307 | 3.4175 | 0.91756
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.63424 | 0.64363 | 0.0070194 | 1.0148 | 651.465 | 14.2492 | 2.8128 | 1.0015
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.63467 | 0.63632 | 0.0059361 | 1.0026 | 651.465 | 14.2492 | 2.8128 | 1.0487
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.63838 | 0.6463 | 0.015901 | 1.0124 | 651.465 | 14.2492 | 2.8128 | 1.1664
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.63545 | 0.65624 | 0.0096854 | 1.0327 | 651.465 | 14.2492 | 2.8128 | 0.9772
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_P07_row8
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio | Albedo_actual
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.71262 | 0.71337 | 0.01282 | 1.0011 | 822.369 | 24.1474 | 1.932 | 1.0264 | 0.20104
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.71177 | 0.70784 | 0.01095 | 0.99448 | 822.369 | 24.1474 | 1.932 | 1.0143 | 0.21465
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.71358 | 0.69744 | 0.015458 | 0.97738 | 822.369 | 24.1474 | 1.932 | 1.1116 | 0.20108
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.71854 | 0.70327 | 0.018318 | 0.97875 | 822.369 | 24.1474 | 1.932 | 1.074 | 0.18924
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.72765 | 0.71544 | 0.015763 | 0.98322 | 845.298 | 26.1993 | 1.9697 | 1.0383 | 0.20199
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.7293 | 0.71729 | 0.016701 | 0.98353 | 845.298 | 26.1993 | 1.9697 | 1.0199 | 0.19409
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.72813 | 0.70251 | 0.015712 | 0.96482 | 845.298 | 26.1993 | 1.9697 | 1.015 | 0.19023
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.72723 | 0.70714 | 0.017425 | 0.97237 | 845.298 | 26.1993 | 1.9697 | 0.99595 | 0.18185
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.6902 | 0.67902 | 0.018591 | 0.98379 | 796.381 | 25.9348 | 1.9765 | 1.0315 | 0.18577
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.68819 | 0.67692 | 0.015295 | 0.98363 | 796.381 | 25.9348 | 1.9765 | 1.0277 | 0.18466
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.68822 | 0.67869 | 0.013837 | 0.98616 | 796.381 | 25.9348 | 1.9765 | 1.0647 | 0.17984
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.68951 | 0.68085 | 0.014605 | 0.98745 | 796.381 | 25.9348 | 1.9765 | 1.0368 | 0.20006
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.68827 | 0.67154 | 0.014819 | 0.97569 | 796.381 | 25.9348 | 1.9765 | 1.0698 | 0.21052
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.67962 | 0.67069 | 0.017994 | 0.98687 | 781.826 | 23.7827 | 1.9514 | 1.0007 | 0.21541
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.68288 | 0.66973 | 0.016094 | 0.98074 | 781.826 | 23.7827 | 1.9514 | 1.0275 | 0.22237
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.68618 | 0.67852 | 0.01392 | 0.98883 | 781.826 | 23.7827 | 1.9514 | 1.0161 | 0.21775
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.68439 | 0.67764 | 0.018604 | 0.99014 | 781.826 | 23.7827 | 1.9514 | 1.1011 | 0.21258
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.62713 | 0.61688 | 0.013657 | 0.98367 | 683.416 | 15.3174 | 2.2291 | 1.0518 | 0.2226
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.62733 | 0.62553 | 0.013614 | 0.99713 | 683.416 | 15.3174 | 2.2291 | 1.0822 | 0.22062
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.62739 | 0.62604 | 0.014542 | 0.99786 | 683.416 | 15.3174 | 2.2291 | 1.0501 | 0.22259
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.62656 | 0.62472 | 0.02289 | 0.99706 | 683.416 | 15.3174 | 2.2291 | 1.0207 | 0.22689
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.49648 | 0.49823 | 0.014039 | 1.0035 | 537.979 | 12.4111 | 2.2953 | 1.0226 | 0.22736
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.50213 | 0.50707 | 0.012651 | 1.0098 | 537.979 | 12.4111 | 2.2953 | 1.0578 | 0.22352
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.49972 | 0.50447 | 0.012741 | 1.0095 | 537.979 | 12.4111 | 2.2953 | 1.0386 | 0.24139
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.5003 | 0.50753 | 0.015686 | 1.0145 | 537.979 | 12.4111 | 2.2953 | 1.0532 | 0.26171
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.50222 | 0.50717 | 0.011164 | 1.0099 | 537.979 | 12.4111 | 2.2953 | 1.0606 | 0.23359
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.41449 | 0.42289 | 0.011621 | 1.0203 | 435.196 | 7.0973 | 2.5547 | 1.0754 | 0.29322
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.41746 | 0.42294 | 0.011862 | 1.0131 | 435.196 | 7.0973 | 2.5547 | 1.0346 | 0.2338
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.41945 | 0.42368 | 0.011358 | 1.0101 | 435.196 | 7.0973 | 2.5547 | 1.006 | 0.24579
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.41957 | 0.42418 | 0.0093117 | 1.011 | 435.196 | 7.0973 | 2.5547 | 1.0262 | 0.44009
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.34494 | 0.35237 | 0.022098 | 1.0215 | 360.138 | 4.7728 | 1.9737 | 1.0097 | 0.60833
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.34504 | 0.35563 | 0.019385 | 1.0307 | 360.138 | 4.7728 | 1.9737 | 0.98271 | 0.32067
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.34384 | 0.3472 | 0.022929 | 1.0098 | 360.138 | 4.7728 | 1.9737 | 1.2006 | 0.26609
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.34776 | 0.35803 | 0.012008 | 1.0295 | 360.138 | 4.7728 | 1.9737 | 2.4211 | 0.63986
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.34413 | 0.34228 | 0.092144 | 0.99461 | 360.138 | 4.7728 | 1.9737 | 1.2189 | 0.64239
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.58224 | 0.59106 | 0.01264 | 1.0151 | 607.817 | 2.6439 | 2.3498 | 1.1053 | 0.39554
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.58025 | 0.59134 | 0.012101 | 1.0191 | 607.817 | 2.6439 | 2.3498 | 1.0818 | 0.3917
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.57833 | 0.59018 | 0.011962 | 1.0205 | 607.817 | 2.6439 | 2.3498 | 1.0655 | 0.39736
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.58025 | 0.59651 | 0.012147 | 1.028 | 607.817 | 2.6439 | 2.3498 | 1.0229 | 0.42006
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.49397 | 0.50719 | 0.025436 | 1.0268 | 529.466 | 8.1543 | 2.3617 | 1.0937 | 0.36541
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.49655 | 0.51107 | 0.025219 | 1.0292 | 529.466 | 8.1543 | 2.3617 | 1.216 | 0.39193
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.49676 | 0.504 | 0.015376 | 1.0146 | 529.466 | 8.1543 | 2.3617 | 1.0436 | 0.16776
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.4916 | 0.49609 | 0.013528 | 1.0091 | 529.466 | 8.1543 | 2.3617 | 1.0295 | 0.17874
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.7903 | 0.77114 | 0.017107 | 0.97576 | 849.963 | 11.8909 | 3.2839 | 1.0206 | 0.18798
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.793 | 0.7779 | 0.012127 | 0.98095 | 849.963 | 11.8909 | 3.2839 | 1.0143 | 0.19201
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.78769 | 0.77766 | 0.013067 | 0.98726 | 849.963 | 11.8909 | 3.2839 | 0.9918 | 0.1907
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.78481 | 0.76449 | 0.012181 | 0.97411 | 849.963 | 11.8909 | 3.2839 | 1.0506 | 0.18178
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.63388 | 0.62941 | 0.014022 | 0.99295 | 696.538 | 16.0347 | 2.3661 | 1.0445 | 0.18184
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.63189 | 0.64259 | 0.01244 | 1.0169 | 696.538 | 16.0347 | 2.3661 | 1.0261 | 0.18693
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.62505 | 0.63201 | 0.010873 | 1.0111 | 696.538 | 16.0347 | 2.3661 | 1.0068 | 0.2797
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.63152 | 0.64076 | 0.012064 | 1.0146 | 696.538 | 16.0347 | 2.3661 | 1.0718 | 0.18455
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_P07_row24_POA
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.74743 | 0.74166 | 0.015543 | 0.99227 | 822.369 | 24.1474 | 1.932 | 1.0226
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.74941 | 0.74037 | 0.015876 | 0.98794 | 822.369 | 24.1474 | 1.932 | 1.0033
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.76619 | 0.74325 | 0.021398 | 0.97005 | 822.369 | 24.1474 | 1.932 | 1.134
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.76164 | 0.74524 | 0.021571 | 0.97847 | 822.369 | 24.1474 | 1.932 | 1.0674
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.76835 | 0.75082 | 0.014259 | 0.97718 | 845.298 | 26.2669 | 1.959 | 1.0446
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.77282 | 0.76064 | 0.02307 | 0.98424 | 845.298 | 26.2669 | 1.959 | 1.0056
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.76653 | 0.74263 | 0.018758 | 0.96883 | 845.298 | 26.2669 | 1.959 | 1.0267
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.76832 | 0.74947 | 0.018499 | 0.97547 | 845.298 | 26.2669 | 1.959 | 1.0127
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.73175 | 0.72551 | 0.018768 | 0.99147 | 796.381 | 25.9348 | 1.9765 | 1.0676
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.724 | 0.71444 | 0.015059 | 0.98679 | 796.381 | 25.9348 | 1.9765 | 1.0382
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.72706 | 0.71492 | 0.012943 | 0.9833 | 796.381 | 25.9348 | 1.9765 | 1.0256
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.7247 | 0.71134 | 0.016619 | 0.98157 | 796.381 | 25.9348 | 1.9765 | 1.0088
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.7312 | 0.714 | 0.019293 | 0.97648 | 796.381 | 25.9348 | 1.9765 | 1.0356
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.7141 | 0.70623 | 0.023978 | 0.98898 | 781.826 | 23.7827 | 1.9514 | 0.99822
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.72451 | 0.71118 | 0.019945 | 0.98161 | 781.826 | 23.7827 | 1.9514 | 1.0166
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.72051 | 0.7179 | 0.017453 | 0.99637 | 781.826 | 23.7827 | 1.9514 | 1.0007
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.72809 | 0.72186 | 0.024745 | 0.99144 | 781.826 | 23.7827 | 1.9514 | 1.0409
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.66828 | 0.65452 | 0.017203 | 0.97941 | 683.416 | 15.3174 | 2.2291 | 1.0478
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.66931 | 0.66564 | 0.0202 | 0.99452 | 683.416 | 15.3174 | 2.2291 | 1.0344
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.67022 | 0.67181 | 0.020262 | 1.0024 | 683.416 | 15.3174 | 2.2291 | 0.99359
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.67004 | 0.66817 | 0.033327 | 0.99721 | 683.416 | 15.3174 | 2.2291 | 1.0015
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.53032 | 0.54268 | 0.029633 | 1.0233 | 537.979 | 12.4111 | 2.2953 | 1.0263
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.53835 | 0.54871 | 0.024012 | 1.0192 | 537.979 | 12.4111 | 2.2953 | 1.0223
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.53935 | 0.54812 | 0.033311 | 1.0163 | 537.979 | 12.4111 | 2.2953 | 1.0124
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.5365 | 0.54585 | 0.039414 | 1.0174 | 537.979 | 12.4111 | 2.2953 | 1.0404
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.53076 | 0.54233 | 0.019928 | 1.0218 | 537.979 | 12.4111 | 2.2953 | 1.0531
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.44786 | 0.46025 | 0.022042 | 1.0276 | 435.196 | 7.0973 | 2.5547 | 1.0225
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.44356 | 0.46025 | 0.019851 | 1.0376 | 435.196 | 7.0973 | 2.5547 | 1.0216
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.44133 | 0.45821 | 0.017624 | 1.0383 | 435.196 | 7.0973 | 2.5547 | 1.0517
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.44458 | 0.46089 | 0.017363 | 1.0367 | 435.196 | 7.0973 | 2.5547 | 0.98691
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.37458 | 0.41581 | 0.059606 | 1.1101 | 360.138 | 4.7728 | 1.9737 | 1.164
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.38199 | 0.40641 | 0.056149 | 1.0639 | 360.138 | 4.7728 | 1.9737 | 0.97856
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.38202 | 0.38561 | 0.073345 | 1.0094 | 360.138 | 4.7728 | 1.9737 | 1.089
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.39024 | 0.3727 | 0.099883 | 0.95505 | 360.138 | 4.7728 | 1.9737 | 1.1166
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.3713 | 0.38406 | 0.073266 | 1.0344 | 360.138 | 4.7728 | 1.9737 | 1.0398
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.6333 | 0.6605 | 0.038989 | 1.0429 | 607.817 | 2.6439 | 2.3498 | 1.136
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.62531 | 0.63481 | 0.025053 | 1.0152 | 607.817 | 2.6439 | 2.3498 | 1.0779
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.6394 | 0.65222 | 0.021196 | 1.0201 | 607.817 | 2.6439 | 2.3498 | 1.0971
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.62747 | 0.64182 | 0.021657 | 1.0229 | 607.817 | 2.6439 | 2.3498 | 1.0601
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.5726 | 0.54623 | 0.099168 | 0.95395 | 529.466 | 8.0916 | 2.3775 | 1.0544
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.5331 | 0.55339 | 0.027728 | 1.0381 | 529.466 | 8.0916 | 2.3775 | 1.1048
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.52977 | 0.54639 | 0.018877 | 1.0314 | 529.466 | 8.0916 | 2.3775 | 1.0378
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.53047 | 0.54001 | 0.026425 | 1.018 | 529.466 | 8.0916 | 2.3775 | 1.0063
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.82536 | 0.80793 | 0.026664 | 0.97888 | 849.963 | 11.8909 | 3.2839 | 0.97518
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.83458 | 0.81923 | 0.021458 | 0.9816 | 849.963 | 11.8909 | 3.2839 | 0.97989
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.82419 | 0.81772 | 0.014708 | 0.99215 | 849.963 | 11.8909 | 3.2839 | 0.99334
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.8235 | 0.81546 | 0.011519 | 0.99024 | 849.963 | 11.8909 | 3.2839 | 1.0138
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.67568 | 0.67416 | 0.014952 | 0.99776 | 696.538 | 16.0347 | 2.3661 | 1.0108
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.66038 | 0.66985 | 0.012894 | 1.0143 | 696.538 | 16.0347 | 2.3661 | 0.98822
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.66816 | 0.67661 | 0.013583 | 1.0126 | 696.538 | 16.0347 | 2.3661 | 0.9867
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.67797 | 0.68622 | 0.014863 | 1.0122 | 696.538 | 16.0347 | 2.3661 | 1.0667
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_P07_row24_Gtotal
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.73047 | 0.71898 | 0.011292 | 0.98428 | 832.7868 | 23.8887 | 1.976 | 1.0425
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.73064 | 0.71402 | 0.0097969 | 0.97725 | 832.7868 | 23.8887 | 1.976 | 1.009
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.73221 | 0.70946 | 0.014538 | 0.96894 | 832.7868 | 23.8887 | 1.976 | 1.0849
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.73564 | 0.71375 | 0.015676 | 0.97025 | 832.7868 | 23.8887 | 1.976 | 1.0522
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.76136 | 0.73682 | 0.015456 | 0.96776 | 877.0629 | 26.1179 | 1.9715 | 1.0343
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.76275 | 0.74077 | 0.014745 | 0.97118 | 877.0629 | 26.1179 | 1.9715 | 1.0231
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.76184 | 0.72839 | 0.015779 | 0.95609 | 877.0629 | 26.1179 | 1.9715 | 1.0078
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.76043 | 0.73212 | 0.013448 | 0.96278 | 877.0629 | 26.1179 | 1.9715 | 1.0343
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.73293 | 0.71253 | 0.01869 | 0.97216 | 837.1392 | 25.9702 | 1.9678 | 1.038
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.73021 | 0.70722 | 0.014377 | 0.96852 | 837.1392 | 25.9702 | 1.9678 | 1.0272
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.72991 | 0.70708 | 0.012327 | 0.96872 | 837.1392 | 25.9702 | 1.9678 | 1.0265
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.7299 | 0.7087 | 0.013165 | 0.97096 | 837.1392 | 25.9702 | 1.9678 | 0.99889
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.73014 | 0.70193 | 0.014626 | 0.96137 | 837.1392 | 25.9702 | 1.9678 | 1.0053
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.72163 | 0.6965 | 0.015377 | 0.96517 | 820.3748 | 23.4107 | 1.9571 | 0.99734
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.72572 | 0.69839 | 0.013477 | 0.96234 | 820.3748 | 23.4107 | 1.9571 | 1.0086
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.7268 | 0.70758 | 0.014693 | 0.97355 | 820.3748 | 23.4107 | 1.9571 | 0.99019
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.7292 | 0.71142 | 0.017596 | 0.97562 | 820.3748 | 23.4107 | 1.9571 | 1.054
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.67285 | 0.65135 | 0.013734 | 0.96805 | 723.3474 | 14.8813 | 2.4372 | 1.0484
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.67775 | 0.66256 | 0.013069 | 0.97758 | 723.3474 | 14.8813 | 2.4372 | 1.0694
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.67638 | 0.66463 | 0.015308 | 0.98263 | 723.3474 | 14.8813 | 2.4372 | 0.9892
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.67377 | 0.66579 | 0.018542 | 0.98816 | 723.3474 | 14.8813 | 2.4372 | 1.0012
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.49955 | 0.50222 | 0.010664 | 1.0053 | 528.7657 | 11.6819 | 2.3946 | 0.9904
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.50599 | 0.5055 | 0.0098067 | 0.99904 | 528.7657 | 11.6819 | 2.3946 | 1.0453
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.50407 | 0.50212 | 0.011912 | 0.99613 | 528.7657 | 11.6819 | 2.3946 | 1.0027
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.50418 | 0.5043 | 0.012592 | 1.0002 | 528.7657 | 11.6819 | 2.3946 | 1.061
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.50625 | 0.50549 | 0.012913 | 0.9985 | 528.7657 | 11.6819 | 2.3946 | 1.0619
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.42411 | 0.4255 | 0.010557 | 1.0033 | 434.4238 | 6.7668 | 2.6569 | 0.98353
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.42623 | 0.42504 | 0.0097464 | 0.9972 | 434.4238 | 6.7668 | 2.6569 | 0.98767
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.42848 | 0.42678 | 0.010982 | 0.99603 | 434.4238 | 6.7668 | 2.6569 | 0.96094
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.42861 | 0.42995 | 0.0097259 | 1.0031 | 434.4238 | 6.7668 | 2.6569 | 0.96528
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.36116 | 0.36074 | 0.025928 | 0.99883 | 369.7939 | 4.7 | 2.0589 | 0.90011
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.363 | 0.36115 | 0.02238 | 0.9949 | 369.7939 | 4.7 | 2.0589 | 0.95053
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.36481 | 0.36499 | 0.03547 | 1.0005 | 369.7939 | 4.7 | 2.0589 | 1.027
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.36499 | 0.36647 | 0.069323 | 1.004 | 369.7939 | 4.7 | 2.0589 | 1.5675
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.35966 | 0.3612 | 0.053836 | 1.0043 | 369.7939 | 4.7 | 2.0589 | 1.0524
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.6125 | 0.60961 | 0.012114 | 0.99529 | 632.3803 | 2.5505 | 2.3458 | 1.1225
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.61315 | 0.60407 | 0.013426 | 0.98519 | 632.3803 | 2.5505 | 2.3458 | 1.0399
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.60963 | 0.61415 | 0.013697 | 1.0074 | 632.3803 | 2.5505 | 2.3458 | 1.1025
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.61017 | 0.6183 | 0.01189 | 1.0133 | 632.3803 | 2.5505 | 2.3458 | 1.0273
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.52327 | 0.51685 | 0.028067 | 0.98773 | 549.1692 | 7.782 | 2.4381 | 1.0393
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.52658 | 0.53718 | 0.028064 | 1.0201 | 549.1692 | 7.782 | 2.4381 | 1.1089
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.52626 | 0.53241 | 0.013687 | 1.0117 | 549.1692 | 7.782 | 2.4381 | 1.0318
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.52206 | 0.52627 | 0.0133 | 1.0081 | 549.1692 | 7.782 | 2.4381 | 0.9875
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.82257 | 0.80099 | 0.016819 | 0.97377 | 882.247 | 11.7063 | 3.3226 | 1.0045
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.827 | 0.8087 | 0.011346 | 0.97788 | 882.247 | 11.7063 | 3.3226 | 0.99716
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.82263 | 0.80925 | 0.011331 | 0.98373 | 882.247 | 11.7063 | 3.3226 | 0.98702
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.82018 | 0.80471 | 0.011404 | 0.98114 | 882.247 | 11.7063 | 3.3226 | 1.0271
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.656 | 0.64971 | 0.011918 | 0.99042 | 708.4881 | 15.8855 | 2.4488 | 1.0245
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.65327 | 0.65021 | 0.012614 | 0.99531 | 708.4881 | 15.8855 | 2.4488 | 1.0167
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.64722 | 0.64351 | 0.01093 | 0.99427 | 708.4881 | 15.8855 | 2.4488 | 0.96398
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.65382 | 0.655 | 0.012298 | 1.0018 | 708.4881 | 15.8855 | 2.4488 | 1.0422
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_P07_row24_Method4
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.73047 | 0.73192 | 0.011638 | 1.002 | 832.7868 | 23.8887 | 1.976
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.73064 | 0.73082 | 0.009467 | 1.0002 | 832.7868 | 23.8887 | 1.976
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.73221 | 0.72463 | 0.014954 | 0.98965 | 832.7868 | 23.8887 | 1.976
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.73564 | 0.72083 | 0.017674 | 0.97987 | 832.7868 | 23.8887 | 1.976
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.76136 | 0.75208 | 0.015023 | 0.98781 | 877.0629 | 26.1179 | 1.9715
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.76275 | 0.75289 | 0.015093 | 0.98707 | 877.0629 | 26.1179 | 1.9715
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.76184 | 0.74835 | 0.0153 | 0.98229 | 877.0629 | 26.1179 | 1.9715
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.76043 | 0.7495 | 0.014104 | 0.98563 | 877.0629 | 26.1179 | 1.9715
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.73293 | 0.72449 | 0.01931 | 0.98848 | 837.1392 | 25.9702 | 1.9678
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.73021 | 0.72449 | 0.014974 | 0.99217 | 837.1392 | 25.9702 | 1.9678
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.72991 | 0.72438 | 0.011502 | 0.99243 | 837.1392 | 25.9702 | 1.9678
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.7299 | 0.72361 | 0.012741 | 0.99138 | 837.1392 | 25.9702 | 1.9678
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.73014 | 0.71952 | 0.01365 | 0.98547 | 837.1392 | 25.9702 | 1.9678
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.72163 | 0.71418 | 0.016223 | 0.98967 | 820.3748 | 23.4107 | 1.9571
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.72572 | 0.71457 | 0.014445 | 0.98464 | 820.3748 | 23.4107 | 1.9571
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.72745 | 0.71723 | 0.014389 | 0.98596 | 820.3748 | 23.4107 | 1.9571
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.7292 | 0.71972 | 0.016535 | 0.987 | 820.3748 | 23.4107 | 1.9571
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.67285 | 0.66224 | 0.014278 | 0.98424 | 723.3474 | 14.8813 | 2.4372
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.67775 | 0.67111 | 0.014297 | 0.99019 | 723.3474 | 14.8813 | 2.4372
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.67638 | 0.66939 | 0.015151 | 0.98967 | 723.3474 | 14.8813 | 2.4372
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.67377 | 0.67397 | 0.017922 | 1.0003 | 723.3474 | 14.8813 | 2.4372
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.49955 | 0.49887 | 0.010929 | 0.99863 | 528.7657 | 11.6819 | 2.3946
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.50599 | 0.50578 | 0.010611 | 0.9996 | 528.7657 | 11.6819 | 2.3946
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.50407 | 0.50504 | 0.01222 | 1.0019 | 528.7657 | 11.6819 | 2.3946
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.50418 | 0.50309 | 0.012627 | 0.99783 | 528.7657 | 11.6819 | 2.3946
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.50625 | 0.50308 | 0.01283 | 0.99374 | 528.7657 | 11.6819 | 2.3946
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.42411 | 0.42357 | 0.0090449 | 0.99873 | 434.4238 | 6.7668 | 2.6569
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.42623 | 0.42334 | 0.0093723 | 0.99322 | 434.4238 | 6.7668 | 2.6569
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.42848 | 0.42456 | 0.010516 | 0.99085 | 434.4238 | 6.7668 | 2.6569
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.42861 | 0.42373 | 0.0097747 | 0.98861 | 434.4238 | 6.7668 | 2.6569
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.36116 | 0.36252 | 0.025345 | 1.0038 | 369.7939 | 4.7 | 2.0589
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.363 | 0.36254 | 0.021099 | 0.99873 | 369.7939 | 4.7 | 2.0589
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.36481 | 0.36726 | 0.033054 | 1.0067 | 369.7939 | 4.7 | 2.0589
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.36499 | 0.35456 | 0.075768 | 0.97142 | 369.7939 | 4.7 | 2.0589
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.35966 | 0.35877 | 0.050864 | 0.99751 | 369.7939 | 4.7 | 2.0589
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.6125 | 0.61617 | 0.012976 | 1.006 | 632.3803 | 2.5505 | 2.3458
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.61315 | 0.61679 | 0.01311 | 1.0059 | 632.3803 | 2.5505 | 2.3458
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.60963 | 0.61754 | 0.013637 | 1.013 | 632.3803 | 2.5505 | 2.3458
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.61017 | 0.61962 | 0.012012 | 1.0155 | 632.3803 | 2.5505 | 2.3458
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.52327 | 0.51764 | 0.028573 | 0.98925 | 549.1692 | 7.782 | 2.4381
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.52658 | 0.52812 | 0.028484 | 1.0029 | 549.1692 | 7.782 | 2.4381
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.52626 | 0.53396 | 0.014599 | 1.0146 | 549.1692 | 7.782 | 2.4381
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.52206 | 0.52738 | 0.012656 | 1.0102 | 549.1692 | 7.782 | 2.4381
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.82257 | 0.80973 | 0.016293 | 0.9844 | 882.247 | 11.7063 | 3.3226
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.827 | 0.8127 | 0.011496 | 0.98272 | 882.247 | 11.7063 | 3.3226
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.82263 | 0.81566 | 0.0119 | 0.99152 | 882.247 | 11.7063 | 3.3226
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.82018 | 0.80919 | 0.011371 | 0.9866 | 882.247 | 11.7063 | 3.3226
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.656 | 0.65098 | 0.012695 | 0.99235 | 708.4881 | 15.8855 | 2.4488
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.65327 | 0.65385 | 0.012528 | 1.0009 | 708.4881 | 15.8855 | 2.4488
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.64722 | 0.64679 | 0.010597 | 0.99935 | 708.4881 | 15.8855 | 2.4488
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.65382 | 0.64874 | 0.01221 | 0.99223 | 708.4881 | 15.8855 | 2.4488
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_P11_row8
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio | ratio_fudge | Albedo_actual
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.72418 | 0.73088 | 0.011872 | 1.0092 | 844.836 | 24.0159 | 2.0037 | 1.0279 | 1.0068 | 0.20104
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.72475 | 0.72532 | 0.0098812 | 1.0008 | 844.836 | 24.0159 | 2.0037 | 1.0298 | 0.99839 | 0.21465
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.72208 | 0.71505 | 0.014947 | 0.99027 | 844.836 | 24.0159 | 2.0037 | 1.074 | 0.9879 | 0.20108
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.72484 | 0.71997 | 0.013444 | 0.99328 | 844.836 | 24.0159 | 2.0037 | 1.079 | 0.9909 | 0.18924
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.74239 | 0.7375 | 0.011621 | 0.99341 | 877.233 | 26.5262 | 1.9931 | 1.0437 | 0.99102 | 0.20199
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.7413 | 0.74034 | 0.016393 | 0.9987 | 877.233 | 26.5262 | 1.9931 | 1.055 | 0.9963 | 0.19409
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.74193 | 0.72539 | 0.016964 | 0.97771 | 877.233 | 26.5262 | 1.9931 | 1.0446 | 0.97536 | 0.19023
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.74079 | 0.72988 | 0.012016 | 0.98528 | 877.233 | 26.5262 | 1.9931 | 1.0137 | 0.98291 | 0.18185
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.7089 | 0.70787 | 0.015439 | 0.99854 | 834.193 | 26.2792 | 2.034 | 1.0617 | 0.99615 | 0.18577
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.71014 | 0.70427 | 0.013908 | 0.99174 | 834.193 | 26.2792 | 2.034 | 1.0452 | 0.98936 | 0.18466
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.70936 | 0.70638 | 0.011021 | 0.9958 | 834.193 | 26.2792 | 2.034 | 1.08 | 0.99341 | 0.17984
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.71242 | 0.70762 | 0.013428 | 0.99327 | 834.193 | 26.2792 | 2.034 | 1.0354 | 0.99088 | 0.20006
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.71077 | 0.69988 | 0.012882 | 0.98467 | 834.193 | 26.2792 | 2.034 | 1.0609 | 0.98231 | 0.21052
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.72176 | 0.70944 | 0.012507 | 0.98293 | 835.036 | 23.9526 | 2.0413 | 1.0043 | 0.98057 | 0.21541
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.72285 | 0.71067 | 0.014345 | 0.98315 | 835.036 | 23.9526 | 2.0413 | 1.0279 | 0.98079 | 0.22237
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.72587 | 0.71851 | 0.013523 | 0.98987 | 835.036 | 23.9526 | 2.0413 | 1.0137 | 0.98749 | 0.21775
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.72721 | 0.71828 | 0.019688 | 0.98772 | 835.036 | 23.9526 | 2.0413 | 1.0586 | 0.98535 | 0.21258
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.66419 | 0.655 | 0.011364 | 0.98616 | 732.985 | 16.29 | 2.2011 | 1.0247 | 0.9838 | 0.2226
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.66748 | 0.66403 | 0.012267 | 0.99483 | 732.985 | 16.29 | 2.2011 | 1.0588 | 0.99244 | 0.22062
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.66848 | 0.66448 | 0.010457 | 0.99401 | 732.985 | 16.29 | 2.2011 | 1.039 | 0.99162 | 0.22259
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.67193 | 0.66387 | 0.023601 | 0.98801 | 732.985 | 16.29 | 2.2011 | 1.0029 | 0.98564 | 0.22689
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.50555 | 0.50074 | 0.013184 | 0.99049 | 540.34 | 12.1034 | 2.2995 | 1.0081 | 0.98811 | 0.22736
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.50758 | 0.50983 | 0.013103 | 1.0044 | 540.34 | 12.1034 | 2.2995 | 1.04 | 1.002 | 0.22352
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.50678 | 0.50716 | 0.012482 | 1.0008 | 540.34 | 12.1034 | 2.2995 | 1.053 | 0.99836 | 0.24139
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.50961 | 0.51029 | 0.013894 | 1.0013 | 540.34 | 12.1034 | 2.2995 | 1.0531 | 0.99893 | 0.26171
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.51073 | 0.50986 | 0.012886 | 0.9983 | 540.34 | 12.1034 | 2.2995 | 1.0627 | 0.99591 | 0.23359
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.4204 | 0.42352 | 0.012668 | 1.0074 | 437.71 | 7.6613 | 2.2698 | 1.0717 | 1.005 | 0.29322
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.422 | 0.42406 | 0.010537 | 1.0049 | 437.71 | 7.6613 | 2.2698 | 1.029 | 1.0025 | 0.2338
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.42472 | 0.4244 | 0.0091191 | 0.99926 | 437.71 | 7.6613 | 2.2698 | 1.004 | 0.99686 | 0.24579
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.42417 | 0.42511 | 0.010648 | 1.0022 | 437.71 | 7.6613 | 2.2698 | 1.0157 | 0.99981 | 0.44009
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.41109 | 0.4108 | 0.016626 | 0.9993 | 422.795 | 5.3307 | 1.8559 | 1.0749 | 0.99691 | 0.60833
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.40634 | 0.41353 | 0.013188 | 1.0177 | 422.795 | 5.3307 | 1.8559 | 1.0342 | 1.0153 | 0.32067
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.40606 | 0.4071 | 0.016658 | 1.0026 | 422.795 | 5.3307 | 1.8559 | 1.0779 | 1.0001 | 0.26609
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.40359 | 0.4117 | 0.027163 | 1.0201 | 422.795 | 5.3307 | 1.8559 | 1.0362 | 1.0177 | 0.63986
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.40176 | 0.40337 | 0.028602 | 1.004 | 422.795 | 5.3307 | 1.8559 | 1.3563 | 1.0016 | 0.64239
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.57977 | 0.58511 | 0.014271 | 1.0092 | 599.796 | 1.8609 | 2.3919 | 1.0679 | 1.0068 | 0.39554
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.57762 | 0.58554 | 0.011332 | 1.0137 | 599.796 | 1.8609 | 2.3919 | 1.0235 | 1.0113 | 0.3917
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.57361 | 0.58471 | 0.012686 | 1.0193 | 599.796 | 1.8609 | 2.3919 | 1.0521 | 1.0169 | 0.39736
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.57725 | 0.59168 | 0.010599 | 1.025 | 599.796 | 1.8609 | 2.3919 | 1.0072 | 1.0225 | 0.42006
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.5649 | 0.57086 | 0.017015 | 1.0106 | 602.896 | 7.4595 | 2.3481 | 0.99295 | 1.0081 | 0.36541
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.56704 | 0.57763 | 0.011936 | 1.0187 | 602.896 | 7.4595 | 2.3481 | 1.0228 | 1.0162 | 0.39193
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.56367 | 0.57217 | 0.012537 | 1.0151 | 602.896 | 7.4595 | 2.3481 | 0.9631 | 1.0126 | 0.16776
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.56112 | 0.56307 | 0.017338 | 1.0035 | 602.896 | 7.4595 | 2.3481 | 1.0369 | 1.0011 | 0.17874
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.80272 | 0.79035 | 0.012806 | 0.98458 | 873.87 | 11.7051 | 3.2699 | 1.0486 | 0.98222 | 0.18798
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.80299 | 0.79734 | 0.0093166 | 0.99296 | 873.87 | 11.7051 | 3.2699 | 1.0292 | 0.99058 | 0.19201
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.80331 | 0.79601 | 0.011706 | 0.99091 | 873.87 | 11.7051 | 3.2699 | 1.0009 | 0.98853 | 0.1907
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.7962 | 0.78346 | 0.010931 | 0.984 | 873.87 | 11.7051 | 3.2699 | 1.0452 | 0.98164 | 0.18178
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.6654 | 0.66692 | 0.010327 | 1.0023 | 740.229 | 15.6427 | 2.4834 | 1.0605 | 0.99989 | 0.18184
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.66932 | 0.67754 | 0.01002 | 1.0123 | 740.229 | 15.6427 | 2.4834 | 1.022 | 1.0099 | 0.18693
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.65846 | 0.66951 | 0.0090368 | 1.0168 | 740.229 | 15.6427 | 2.4834 | 1.0135 | 1.0144 | 0.2797
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.66243 | 0.67773 | 0.00995 | 1.0231 | 740.229 | 15.6427 | 2.4834 | 1.011 | 1.0206 | 0.18455
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_P11_row24_POA
DATE FROM ISO |  | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.75977 | 0.75997 | 0.012104 | 1.0003 | 844.836 | 24.0159 | 2.0037 | 1.0339
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.76067 | 0.75823 | 0.0092902 | 0.9968 | 844.836 | 24.0159 | 2.0037 | 1.0319
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.76293 | 0.76117 | 0.014465 | 0.9977 | 844.836 | 24.0159 | 2.0037 | 1.1088
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.76449 | 0.76306 | 0.012469 | 0.99813 | 844.836 | 24.0159 | 2.0037 | 1.0887
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.7801 | 0.77497 | 0.012098 | 0.99343 | 877.233 | 26.5262 | 1.9931 | 1.0653
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.78278 | 0.78498 | 0.013017 | 1.0028 | 877.233 | 26.5262 | 1.9931 | 1.053
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.78088 | 0.76622 | 0.015965 | 0.98122 | 877.233 | 26.5262 | 1.9931 | 1.0276
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.78208 | 0.77304 | 0.013614 | 0.98844 | 877.233 | 26.5262 | 1.9931 | 1.0323
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.75268 | 0.75445 | 0.013274 | 1.0024 | 834.193 | 26.2792 | 2.034 | 1.0935
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.7494 | 0.7427 | 0.014522 | 0.99105 | 834.193 | 26.2792 | 2.034 | 1.0545
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.75061 | 0.7438 | 0.011584 | 0.99094 | 834.193 | 26.2792 | 2.034 | 1.0787
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.7501 | 0.74015 | 0.013149 | 0.98673 | 834.193 | 26.2792 | 2.034 | 1.0109
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.75112 | 0.74286 | 0.011787 | 0.989 | 834.193 | 26.2792 | 2.034 | 1.054
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.75768 | 0.74836 | 0.017542 | 0.9877 | 835.036 | 23.9526 | 2.0413 | 1.0162
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.7636 | 0.75397 | 0.010356 | 0.98738 | 835.036 | 23.9526 | 2.0413 | 1.0456
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.76335 | 0.76012 | 0.012843 | 0.99577 | 835.036 | 23.9526 | 2.0413 | 1.0154
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.76896 | 0.76426 | 0.015562 | 0.99388 | 835.036 | 23.9526 | 2.0413 | 1.0547
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.70632 | 0.69411 | 0.014589 | 0.98272 | 732.985 | 16.29 | 2.2011 | 1.046
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.71148 | 0.70525 | 0.014732 | 0.99125 | 732.985 | 16.29 | 2.2011 | 1.0561
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.70913 | 0.71051 | 0.012932 | 1.0019 | 732.985 | 16.29 | 2.2011 | 1.0146
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.71381 | 0.70919 | 0.018863 | 0.99354 | 732.985 | 16.29 | 2.2011 | 1.013
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.53934 | 0.54523 | 0.026479 | 1.0109 | 540.34 | 12.1034 | 2.2995 | 0.99985
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.5433 | 0.55131 | 0.01559 | 1.0147 | 540.34 | 12.1034 | 2.2995 | 1.0358
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.54615 | 0.55092 | 0.01869 | 1.0087 | 540.34 | 12.1034 | 2.2995 | 1.0321
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.54172 | 0.54854 | 0.020866 | 1.0126 | 540.34 | 12.1034 | 2.2995 | 1.057
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.54073 | 0.54483 | 0.017298 | 1.0076 | 540.34 | 12.1034 | 2.2995 | 1.0543
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.45489 | 0.46075 | 0.019896 | 1.0129 | 437.71 | 7.6613 | 2.2698 | 1.0235
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.45305 | 0.46163 | 0.01554 | 1.0189 | 437.71 | 7.6613 | 2.2698 | 1.026
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.44817 | 0.4593 | 0.010645 | 1.0248 | 437.71 | 7.6613 | 2.2698 | 1.0484
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.45336 | 0.46221 | 0.013125 | 1.0195 | 437.71 | 7.6613 | 2.2698 | 0.98781
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.45471 | 0.48325 | 0.029734 | 1.0628 | 422.795 | 5.3307 | 1.8559 | 1.1107
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.45216 | 0.47064 | 0.02582 | 1.0409 | 422.795 | 5.3307 | 1.8559 | 1.0395
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.46037 | 0.45197 | 0.029779 | 0.98176 | 422.795 | 5.3307 | 1.8559 | 1.029
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.45786 | 0.43492 | 0.078559 | 0.9499 | 422.795 | 5.3307 | 1.8559 | 1.0053
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.45323 | 0.44882 | 0.050038 | 0.99028 | 422.795 | 5.3307 | 1.8559 | 1.0827
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.63118 | 0.65597 | 0.028405 | 1.0393 | 599.796 | 1.8609 | 2.3919 | 1.1187
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.63555 | 0.62897 | 0.029463 | 0.98964 | 599.796 | 1.8609 | 2.3919 | 1.0744
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.64598 | 0.64791 | 0.033205 | 1.003 | 599.796 | 1.8609 | 2.3919 | 1.1156
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.61994 | 0.63651 | 0.016883 | 1.0267 | 599.796 | 1.8609 | 2.3919 | 1.0505
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.61364 | 0.62903 | 0.01661 | 1.0251 | 602.896 | 7.4595 | 2.3481 | 1.0657
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.6146 | 0.62153 | 0.012976 | 1.0113 | 602.896 | 7.4595 | 2.3481 | 1.0267
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.61526 | 0.61421 | 0.022035 | 0.99828 | 602.896 | 7.4595 | 2.3481 | 0.99084
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.60115 | 0.6072 | 0.018274 | 1.0101 | 602.896 | 7.4595 | 2.3481 | 1.0248
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.84226 | 0.82719 | 0.015342 | 0.98211 | 873.87 | 11.7051 | 3.2699 | 0.99477
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.84522 | 0.83911 | 0.0098233 | 0.99277 | 873.87 | 11.7051 | 3.2699 | 0.99858
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.83976 | 0.83772 | 0.011113 | 0.99758 | 873.87 | 11.7051 | 3.2699 | 1.0095
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.83893 | 0.83534 | 0.0075685 | 0.99572 | 873.87 | 11.7051 | 3.2699 | 1.0691
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.71086 | 0.71317 | 0.0090348 | 1.0033 | 740.229 | 15.6427 | 2.4834 | 1.0588
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.7063 | 0.70589 | 0.0083756 | 0.99942 | 740.229 | 15.6427 | 2.4834 | 1.0075
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.70434 | 0.71607 | 0.0085764 | 1.0167 | 740.229 | 15.6427 | 2.4834 | 1.0117
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.70964 | 0.72546 | 0.0074496 | 1.0223 | 740.229 | 15.6427 | 2.4834 | 1.0357

## SAM_S02_row24_POA
DATE FROM ISO |  | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70853 | 0.70606 | 0.0056092 | 0.99651 | 776.236 | 23.7712 | 1.9095
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.70958 | 0.70501 | 0.0062542 | 0.99357 | 776.236 | 23.7712 | 1.9095
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.71037 | 0.70774 | 0.010332 | 0.99631 | 776.236 | 23.7712 | 1.9095
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70919 | 0.71044 | 0.0096959 | 1.0018 | 776.236 | 23.7712 | 1.9095
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.78099 | 0.77874 | 0.0059696 | 0.99711 | 882.592 | 26.5955 | 1.9709
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.7836 | 0.7889 | 0.0086976 | 1.0068 | 882.592 | 26.5955 | 1.9709
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.78222 | 0.77008 | 0.0090068 | 0.98449 | 882.592 | 26.5955 | 1.9709
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.78166 | 0.77673 | 0.006972 | 0.99368 | 882.592 | 26.5955 | 1.9709
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.73717 | 0.74673 | 0.012964 | 1.013 | 824.323 | 26.5336 | 2.0233
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.73863 | 0.73548 | 0.0080908 | 0.99574 | 824.323 | 26.5336 | 2.0233
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.73931 | 0.73583 | 0.0069146 | 0.99529 | 824.323 | 26.5336 | 2.0233
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.73799 | 0.73242 | 0.0073999 | 0.99246 | 824.323 | 26.5336 | 2.0233
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.74286 | 0.73515 | 0.0079177 | 0.98963 | 824.323 | 26.5336 | 2.0233
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.74564 | 0.73263 | 0.0090742 | 0.98256 | 814.178 | 23.1048 | 2.0073
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.74623 | 0.73902 | 0.0085213 | 0.99034 | 814.178 | 23.1048 | 2.0073
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.74636 | 0.74597 | 0.010402 | 0.99948 | 814.178 | 23.1048 | 2.0073
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.74939 | 0.74996 | 0.011272 | 1.0008 | 814.178 | 23.1048 | 2.0073
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.67815 | 0.66909 | 0.012708 | 0.98663 | 703.194 | 16.1264 | 2.1092
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.68275 | 0.68004 | 0.015481 | 0.99603 | 703.194 | 16.1264 | 2.1092
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.68047 | 0.68428 | 0.013466 | 1.0056 | 703.194 | 16.1264 | 2.1092
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.68252 | 0.68316 | 0.025166 | 1.0009 | 703.194 | 16.1264 | 2.1092
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.53031 | 0.53753 | 0.021352 | 1.0136 | 531.017 | 11.6822 | 2.308
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.54098 | 0.54343 | 0.016205 | 1.0045 | 531.017 | 11.6822 | 2.308
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.54136 | 0.5431 | 0.015053 | 1.0032 | 531.017 | 11.6822 | 2.308
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.53611 | 0.54093 | 0.024281 | 1.009 | 531.017 | 11.6822 | 2.308
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.53271 | 0.53698 | 0.024268 | 1.008 | 531.017 | 11.6822 | 2.308
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.46317 | 0.46641 | 0.018464 | 1.007 | 443.633 | 8.0486 | 2.3481
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.46443 | 0.46724 | 0.022304 | 1.006 | 443.633 | 8.0486 | 2.3481
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.45512 | 0.46478 | 0.019594 | 1.0212 | 443.633 | 8.0486 | 2.3481
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.46026 | 0.4676 | 0.02146 | 1.016 | 443.633 | 8.0486 | 2.3481
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.49981 | 0.53135 | 0.046766 | 1.0631 | 465.967 | 4.544 | 1.8323
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.50674 | 0.5141 | 0.041676 | 1.0145 | 465.967 | 4.544 | 1.8323
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.488 | 0.4947 | 0.022295 | 1.0137 | 465.967 | 4.544 | 1.8323
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.48261 | 0.48191 | 0.041019 | 0.99855 | 465.967 | 4.544 | 1.8323
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.50153 | 0.49835 | 0.049791 | 0.99365 | 465.967 | 4.544 | 1.8323
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.6862 | 0.71202 | 0.04055 | 1.0376 | 654.071 | 1.5972 | 2.222
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.67538 | 0.68185 | 0.019099 | 1.0096 | 654.071 | 1.5972 | 2.222
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.68715 | 0.70432 | 0.024628 | 1.025 | 654.071 | 1.5972 | 2.222
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.67731 | 0.68959 | 0.017034 | 1.0181 | 654.071 | 1.5972 | 2.222
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.52968 | 0.52166 | 0.085199 | 0.98487 | 492.688 | 7.1792 | 2.4514
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.50224 | 0.52159 | 0.017916 | 1.0385 | 492.688 | 7.1792 | 2.4514
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.50063 | 0.51451 | 0.014503 | 1.0277 | 492.688 | 7.1792 | 2.4514
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.50613 | 0.50839 | 0.0094367 | 1.0045 | 492.688 | 7.1792 | 2.4514
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.79854 | 0.79285 | 0.0073103 | 0.99288 | 830.988 | 11.9278 | 3.2838
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.80197 | 0.80357 | 0.0064401 | 1.002 | 830.988 | 11.9278 | 3.2838
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.80049 | 0.80195 | 0.0070096 | 1.0018 | 830.988 | 11.9278 | 3.2838
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.79783 | 0.79957 | 0.0063224 | 1.0022 | 830.988 | 11.9278 | 3.2838
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.59981 | 0.60799 | 0.0083773 | 1.0136 | 618.299 | 15.7917 | 2.4727
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.59835 | 0.60402 | 0.0099163 | 1.0095 | 618.299 | 15.7917 | 2.4727
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.60708 | 0.60912 | 0.012671 | 1.0034 | 618.299 | 15.7917 | 2.4727
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.60259 | 0.61977 | 0.011947 | 1.0285 | 618.299 | 15.7917 | 2.4727