## Figures
SAM00 model results | [7 empty] | SAMTMYA01 model results - Row 2+4
Row | Method | ASTM / IEC | MBE | RMSE |  |  |  | Row | Method | ASTM / IEC | MBE | RMSE |  | NEW Refmod is 2.3% lower than Gtotal based on back covered field comparison. | OLD Refmod is 3.5% higher than Gtotal based on Spire point
8 | Tamb | ASTM | 0 | 1.15 | <- Mono baseline |  |  | 8 | Tamb | ASTM | -0.03 | 1.31 | <- Mono baseline
8 | Tamb | IEC | 4.8 | 3.83 |  |  |  | 8 | Tmod | ASTM | 0.59 | 1.63
8 | Tmod | ASTM | 0.65 | 1.48 |  |  |  | 2+4 | POA | ASTM | 0.82 | 2.2 | <- Method 1
8 | Tmod | IEC | 5 | 3.76 |  |  |  | 2+4 | Gtotal | ASTM | -1.66 | 1.33 | <- Method 2
8 | Tmod | ASTM Method3 | 0.02 | 0.83 | <- PVSyst comparison for method3 |  |  | 2+4 | Method4 | ASTM | -0.86 | 0.9 | <- Method 4
2+4 | POA | ASTM | 0.36 | 1.54 | <- Method 1
2+4 | POA | IEC | 2.84 | 4.95
2+4 | AlbRegress | ASTM | -0.59 | 1.84 |  |  |  | SAMP00 model results - Row 2+4
2+4 | Gtotal | ASTM | -1.51 | 1.2 | <- Method 2 |  | ` | Row | Method | ASTM / IEC | MBE | RMSE
2+4 | Gtotal | IEC | 2.89 | 3.07 |  |  |  | 8 | Tamb | ASTM | -0.18 | 1.62 | <- Mono baseline
2+4 | Method4 | ASTM | -0.63 | 0.98 | <- Method 4 |  |  | 8 | Tmod | ASTM | 0.04 | 1.85
4 | Method3 | ASTM | 4.47 | 3.7 | <- Method 3, PVSyst |  |  | 2+4 | POA | ASTM | 5.68 | 3.29 | <- Method 1
4 | M3 Grear regression | ASTM | 1.74 | 2.07 | <- Method 3 w Grear as an extra regressor |  |  | 2+4 | Gtotal | ASTM | -1.18 | 1.39 | <- Method 2
[8 empty] | 2+4 | Method4 | ASTM | -0.51 | 0.67 | <- Method 4
ROW 2+4 ASTM ANALYSIS
ROW 4 ASTM ANALYSIS (OLD 8/11 RC's)
ROW 2 ANALYSIS (OLD 8/11 RC's)
|  |  | NEW FILTERING |  | OLD FILTERING
| Row | Method | MBE | RMSE | MBE | RMSE
| 8 | Monofacial (baseline) | 0 | 1.16 | -0.01 | 1.05
| 4 | Method 1 | 1.19 | 2.51 | 1.69 | 2.49
| 4 | Method 2 | -0.24 | 1.71 | -0.47 | 1.33
| 4 | Method 4 | 0.34 | 0.96 | 0.18 | 0.71
| 2 | Method 1 | -0.6 | 1.59 | -0.23 | 1.8
| 2 | Method 2 | -2.52 | 1.23 | -2.63 | 1.16
| 2 | Method 4 | -1.69 | 1.22 | -1.75 | 1.06

## SAM_00_row8
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio | Albedo
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.6684 | 0.67655 | 0.011707 | 1.0122 | 772.039 | 23.7608 | 1.9134 | 1.0377 | 0.20104
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.66923 | 0.67119 | 0.011566 | 1.0029 | 772.039 | 23.7608 | 1.9134 | 1.0114 | 0.21465
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.66395 | 0.65966 | 0.012204 | 0.99354 | 772.039 | 23.7608 | 1.9134 | 1.0605 | 0.20108
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.66475 | 0.66638 | 0.014107 | 1.0024 | 772.039 | 23.7608 | 1.9134 | 1.0521 | 0.18924
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.74262 | 0.7393 | 0.012577 | 0.99553 | 880.138 | 26.5799 | 1.9714 | 1.0276 | 0.20199
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.74032 | 0.74226 | 0.012613 | 1.0026 | 880.138 | 26.5799 | 1.9714 | 1.0397 | 0.19409
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.74184 | 0.72745 | 0.01603 | 0.98061 | 880.138 | 26.5799 | 1.9714 | 1.0429 | 0.19023
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.74089 | 0.73183 | 0.011499 | 0.98776 | 880.138 | 26.5799 | 1.9714 | 1.0293 | 0.18185
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.69891 | 0.70058 | 0.012389 | 1.0024 | 824.619 | 26.4766 | 2.0122 | 1.0875 | 0.18577
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.7028 | 0.69725 | 0.014015 | 0.99209 | 824.619 | 26.4766 | 2.0122 | 1.0491 | 0.18466
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.70434 | 0.69865 | 0.011296 | 0.99192 | 824.619 | 26.4766 | 2.0122 | 1.0761 | 0.17984
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.70505 | 0.70031 | 0.013909 | 0.99327 | 824.619 | 26.4766 | 2.0122 | 1.053 | 0.20006
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.70596 | 0.69244 | 0.011851 | 0.98085 | 824.619 | 26.4766 | 2.0122 | 1.0801 | 0.21052
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.70941 | 0.6957 | 0.015364 | 0.98067 | 815.029 | 23.0289 | 1.9999 | 0.99802 | 0.21541
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.70993 | 0.69707 | 0.011793 | 0.98189 | 815.029 | 23.0289 | 1.9999 | 1.0187 | 0.22237
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.71132 | 0.70603 | 0.011871 | 0.99256 | 815.029 | 23.0289 | 1.9999 | 1.0376 | 0.21775
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.71247 | 0.70501 | 0.015381 | 0.98953 | 815.029 | 23.0289 | 1.9999 | 1.0713 | 0.21258
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.62836 | 0.62394 | 0.012716 | 0.99297 | 694.233 | 15.9432 | 2.0906 | 1.0489 | 0.2226
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.63474 | 0.63208 | 0.011537 | 0.99581 | 694.233 | 15.9432 | 2.0906 | 1.0817 | 0.22062
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.63329 | 0.63233 | 0.011913 | 0.99849 | 694.233 | 15.9432 | 2.0906 | 1.0304 | 0.22259
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.63539 | 0.63141 | 0.014407 | 0.99374 | 694.233 | 15.9432 | 2.0906 | 1.0164 | 0.22689
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.49745 | 0.4899 | 0.01762 | 0.98483 | 527.116 | 11.5588 | 2.3256 | 1.0041 | 0.22736
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.49828 | 0.49923 | 0.0072211 | 1.0019 | 527.116 | 11.5588 | 2.3256 | 1.0723 | 0.22352
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.49716 | 0.49628 | 0.0080386 | 0.99822 | 527.116 | 11.5588 | 2.3256 | 1.0292 | 0.24139
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.49966 | 0.49969 | 0.0074126 | 1.0001 | 527.116 | 11.5588 | 2.3256 | 1.0552 | 0.26171
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.49991 | 0.49925 | 0.0068519 | 0.99869 | 527.116 | 11.5588 | 2.3256 | 1.0769 | 0.23359
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.42543 | 0.42696 | 0.0069544 | 1.0036 | 441.242 | 7.7998 | 2.3424 | 1.0646 | 0.29322
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.42513 | 0.42735 | 0.0049523 | 1.0052 | 441.242 | 7.7998 | 2.3424 | 1.0189 | 0.2338
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.42624 | 0.42756 | 0.0050786 | 1.0031 | 441.242 | 7.7998 | 2.3424 | 1.025 | 0.24579
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.42711 | 0.42831 | 0.0038078 | 1.0028 | 441.242 | 7.7998 | 2.3424 | 1.0887 | 0.44009
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.43071 | 0.42802 | 0.006451 | 0.99375 | 439.731 | 4.2623 | 1.8593 | 1.0458 | 0.60833
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.42603 | 0.43107 | 0.0065922 | 1.0118 | 439.731 | 4.2623 | 1.8593 | 1.0473 | 0.32067
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.42354 | 0.42315 | 0.0086048 | 0.99908 | 439.731 | 4.2623 | 1.8593 | 1.0616 | 0.26609
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.42276 | 0.4292 | 0.010691 | 1.0152 | 439.731 | 4.2623 | 1.8593 | 1.0249 | 0.63986
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.42146 | 0.42162 | 0.0095088 | 1.0004 | 439.731 | 4.2623 | 1.8593 | 1.2046 | 0.64239
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.63734 | 0.64239 | 0.0071914 | 1.0079 | 661.113 | 1.5164 | 2.2028 | 1.0922 | 0.39554
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.64257 | 0.64103 | 0.0084184 | 0.9976 | 661.113 | 1.5164 | 2.2028 | 1.1045 | 0.3917
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.63445 | 0.64139 | 0.011318 | 1.0109 | 661.113 | 1.5164 | 2.2028 | 1.0706 | 0.39736
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.63651 | 0.64612 | 0.00887 | 1.0151 | 661.113 | 1.5164 | 2.2028 | 1.0177 | 0.42006
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.46325 | 0.46732 | 0.01602 | 1.0088 | 483.283 | 6.971 | 2.4579 | 1.1103 | 0.36541
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.45818 | 0.47217 | 0.016204 | 1.0305 | 483.283 | 6.971 | 2.4579 | 1.0651 | 0.39193
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.45711 | 0.46548 | 0.010965 | 1.0183 | 483.283 | 6.971 | 2.4579 | 0.99193 | 0.16776
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.46098 | 0.45475 | 0.010917 | 0.98648 | 483.283 | 6.971 | 2.4579 | 0.92842 | 0.17874
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.76267 | 0.75782 | 0.010562 | 0.99363 | 833.145 | 11.9278 | 3.2838 | 1.0358 | 0.18798
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.76661 | 0.76416 | 0.012897 | 0.9968 | 833.145 | 11.9278 | 3.2838 | 1.0389 | 0.19201
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.76701 | 0.76494 | 0.010518 | 0.9973 | 833.145 | 11.9278 | 3.2838 | 1.0238 | 0.1907
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.76185 | 0.75122 | 0.01079 | 0.98606 | 833.145 | 11.9278 | 3.2838 | 1.0311 | 0.18178
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.54892 | 0.55158 | 0.011838 | 1.0049 | 602.763 | 15.7651 | 2.4656 | 1.0579 | 0.18184
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.55789 | 0.56595 | 0.018864 | 1.0144 | 602.763 | 15.7651 | 2.4656 | 1.0263 | 0.18693
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.54896 | 0.5556 | 0.013942 | 1.0121 | 602.763 | 15.7651 | 2.4656 | 1.0508 | 0.2797
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.54446 | 0.5636 | 0.0087695 | 1.0352 | 602.763 | 15.7651 | 2.4656 | 1.0382 | 0.18455
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row8_Tmod
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.66236 | 0.6711 | 0.014578 | 1.0132 | 752.65 | 38.3508 | 1.9451 | 1.0281
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.66097 | 0.66718 | 0.011997 | 1.0094 | 752.65 | 38.3508 | 1.9451 | 1.0135
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.66005 | 0.65873 | 0.015578 | 0.998 | 752.65 | 38.3508 | 1.9451 | 1.0747
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.66038 | 0.66809 | 0.025486 | 1.0117 | 752.65 | 38.3508 | 1.9451 | 1.0736
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.77552 | 0.77577 | 0.020787 | 1.0003 | 891.611 | 41.1388 | 1.9991 | 1.0264
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.7711 | 0.76478 | 0.022182 | 0.9918 | 891.611 | 41.1388 | 1.9991 | 1.05
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.77165 | 0.75958 | 0.024975 | 0.98437 | 891.611 | 41.1388 | 1.9991 | 1.045
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.76405 | 0.75104 | 0.013572 | 0.98297 | 891.611 | 41.1388 | 1.9991 | 1.0277
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.71162 | 0.70829 | 0.018008 | 0.99533 | 820.232 | 40.3392 | 2.0625 | 1.065
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.71875 | 0.70365 | 0.014861 | 0.97899 | 820.232 | 40.3392 | 2.0625 | 1.0304
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.71722 | 0.7155 | 0.018144 | 0.99761 | 820.232 | 40.3392 | 2.0625 | 1.0928
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.71749 | 0.716 | 0.020381 | 0.99793 | 820.232 | 40.3392 | 2.0625 | 1.0476
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.7187 | 0.70678 | 0.018754 | 0.98341 | 820.232 | 40.3392 | 2.0625 | 1.0853
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.70818 | 0.69382 | 0.01978 | 0.97972 | 796.738 | 36.1038 | 2.0268 | 1.0105
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.70858 | 0.70447 | 0.014253 | 0.9942 | 796.738 | 36.1038 | 2.0268 | 1.0183
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.70967 | 0.71751 | 0.014812 | 1.011 | 796.738 | 36.1038 | 2.0268 | 1.0469
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.70872 | 0.7094 | 0.019785 | 1.001 | 796.738 | 36.1038 | 2.0268 | 1.0911
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.63078 | 0.63241 | 0.015996 | 1.0026 | 685.048 | 27.303 | 2.2185 | 1.0592
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.63744 | 0.64326 | 0.014594 | 1.0091 | 685.048 | 27.303 | 2.2185 | 1.0685
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.63711 | 0.64279 | 0.013018 | 1.0089 | 685.048 | 27.303 | 2.2185 | 1.0408
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.63882 | 0.64203 | 0.015708 | 1.005 | 685.048 | 27.303 | 2.2185 | 1.0206
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.50641 | 0.49989 | 0.017769 | 0.98713 | 530.11 | 20.7103 | 2.4843 | 0.99882
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.50682 | 0.51415 | 0.008117 | 1.0145 | 530.11 | 20.7103 | 2.4843 | 1.0617
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.50625 | 0.50809 | 0.0081652 | 1.0036 | 530.11 | 20.7103 | 2.4843 | 1.0381
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.50785 | 0.50893 | 0.0097313 | 1.0021 | 530.11 | 20.7103 | 2.4843 | 1.0479
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.50892 | 0.51039 | 0.0079357 | 1.0029 | 530.11 | 20.7103 | 2.4843 | 1.0653
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.44617 | 0.44782 | 0.0069783 | 1.0037 | 460.615 | 17.0733 | 2.4814 | 1.1193
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.44651 | 0.45021 | 0.0048551 | 1.0083 | 460.615 | 17.0733 | 2.4814 | 1.0423
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.4482 | 0.44892 | 0.0063586 | 1.0016 | 460.615 | 17.0733 | 2.4814 | 1.0373
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.44785 | 0.44965 | 0.0055058 | 1.004 | 460.615 | 17.0733 | 2.4814 | 1.0874
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.46278 | 0.46765 | 0.0093516 | 1.0105 | 472.209 | 13.5353 | 1.9494 | 0.97474
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.46264 | 0.46949 | 0.0063338 | 1.0148 | 472.209 | 13.5353 | 1.9494 | 1.0947
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.46011 | 0.46129 | 0.0075576 | 1.0026 | 472.209 | 13.5353 | 1.9494 | 1.0775
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.45862 | 0.46701 | 0.010832 | 1.0183 | 472.209 | 13.5353 | 1.9494 | 1.0185
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.45633 | 0.4632 | 0.0087654 | 1.0151 | 472.209 | 13.5353 | 1.9494 | 1.1428
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.63451 | 0.6519 | 0.0081902 | 1.0274 | 650.24 | 12.9264 | 2.3164 | 1.0872
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.63881 | 0.65005 | 0.0098968 | 1.0176 | 650.24 | 12.9264 | 2.3164 | 1.0648
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.62674 | 0.64745 | 0.0087597 | 1.033 | 650.24 | 12.9264 | 2.3164 | 1.0974
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.63467 | 0.66681 | 0.01113 | 1.0506 | 650.24 | 12.9264 | 2.3164 | 1.0232
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.45803 | 0.46533 | 0.012318 | 1.0159 | 477.059 | 16.664 | 2.4707 | 1.1328
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.45416 | 0.47185 | 0.01773 | 1.0389 | 477.059 | 16.664 | 2.4707 | 1.0392
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.45334 | 0.46464 | 0.011834 | 1.0249 | 477.059 | 16.664 | 2.4707 | 1.0178
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.45728 | 0.44947 | 0.012056 | 0.98293 | 477.059 | 16.664 | 2.4707 | 0.9253
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.82368 | 0.82426 | 0.011811 | 1.0007 | 884.741 | 24.1614 | 3.4061 | 1.0419
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.82477 | 0.83704 | 0.015591 | 1.0149 | 884.741 | 24.1614 | 3.4061 | 1.0228
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.82665 | 0.82871 | 0.012646 | 1.0025 | 884.741 | 24.1614 | 3.4061 | 1.0376
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.82133 | 0.82889 | 0.012386 | 1.0092 | 884.741 | 24.1614 | 3.4061 | 1.0498
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.56523 | 0.57251 | 0.015536 | 1.0129 | 617.469 | 26.6758 | 2.4941 | 1.0669
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.57961 | 0.58263 | 0.027665 | 1.0052 | 617.469 | 26.6758 | 2.4941 | 1.0113
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.5697 | 0.57516 | 0.019482 | 1.0096 | 617.469 | 26.6758 | 2.4941 | 1.0675
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.5645 | 0.58606 | 0.011305 | 1.0382 | 617.469 | 26.6758 | 2.4941 | 1.0409
[5 empty] | 1.0065 | 666.2243 | 26.1669
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row2+4_POA
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70519 | 0.7028 | 0.006146 | 0.9966 | 772.039 | 23.7608 | 1.9134 | 1.0116
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.70682 | 0.70188 | 0.0062306 | 0.99301 | 772.039 | 23.7608 | 1.9134 | 1.0071
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.70766 | 0.70446 | 0.010811 | 0.99547 | 772.039 | 23.7608 | 1.9134 | 1.0544
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70639 | 0.70717 | 0.010804 | 1.0011 | 772.039 | 23.7608 | 1.9134 | 1.0324
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.77957 | 0.77692 | 0.0062757 | 0.9966 | 880.138 | 26.5799 | 1.9714 | 1.0324
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.78238 | 0.78708 | 0.0088666 | 1.006 | 880.138 | 26.5799 | 1.9714 | 1.0341
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.78099 | 0.7683 | 0.009528 | 0.98374 | 880.138 | 26.5799 | 1.9714 | 1.0381
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.78012 | 0.77497 | 0.0064664 | 0.9934 | 880.138 | 26.5799 | 1.9714 | 1.0234
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.73794 | 0.7469 | 0.012492 | 1.0121 | 824.619 | 26.4766 | 2.0122 | 1.0711
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.7394 | 0.73565 | 0.007835 | 0.99492 | 824.619 | 26.4766 | 2.0122 | 1.0504
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.74011 | 0.73601 | 0.00682 | 0.99446 | 824.619 | 26.4766 | 2.0122 | 1.0719
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.73872 | 0.7326 | 0.0077212 | 0.9917 | 824.619 | 26.4766 | 2.0122 | 1.0105
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.74367 | 0.73544 | 0.0078269 | 0.98893 | 824.619 | 26.4766 | 2.0122 | 1.0402
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.74697 | 0.73334 | 0.0095463 | 0.98175 | 815.029 | 23.0289 | 1.9999 | 0.99632
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.74805 | 0.73984 | 0.0085545 | 0.98903 | 815.029 | 23.0289 | 1.9999 | 1.0204
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.74768 | 0.74675 | 0.010409 | 0.99875 | 815.029 | 23.0289 | 1.9999 | 1.0145
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.75062 | 0.75077 | 0.011439 | 1.0002 | 815.029 | 23.0289 | 1.9999 | 1.0271
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.67174 | 0.66173 | 0.011768 | 0.9851 | 694.233 | 15.9432 | 2.0906 | 1.0383
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.67618 | 0.67268 | 0.014713 | 0.99483 | 694.233 | 15.9432 | 2.0906 | 1.0245
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.67346 | 0.67804 | 0.014379 | 1.0068 | 694.233 | 15.9432 | 2.0906 | 1.0011
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.67506 | 0.6756 | 0.024886 | 1.0008 | 694.233 | 15.9432 | 2.0906 | 1.0053
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.53015 | 0.53416 | 0.023463 | 1.0076 | 527.116 | 11.5588 | 2.3256 | 0.99863
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.53785 | 0.54012 | 0.014488 | 1.0042 | 527.116 | 11.5588 | 2.3256 | 1.0126
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.53844 | 0.53973 | 0.013814 | 1.0024 | 527.116 | 11.5588 | 2.3256 | 0.99749
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.53243 | 0.53618 | 0.023812 | 1.007 | 527.116 | 11.5588 | 2.3256 | 1.0235
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.53306 | 0.53371 | 0.022495 | 1.0012 | 527.116 | 11.5588 | 2.3256 | 1.0411
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.46262 | 0.4644 | 0.017113 | 1.0038 | 441.242 | 7.7998 | 2.3424 | 1.0257
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.46298 | 0.46502 | 0.022947 | 1.0044 | 441.242 | 7.7998 | 2.3424 | 0.94334
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.45327 | 0.46275 | 0.021052 | 1.0209 | 441.242 | 7.7998 | 2.3424 | 0.99204
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.45835 | 0.46558 | 0.024011 | 1.0158 | 441.242 | 7.7998 | 2.3424 | 0.9896
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.47429 | 0.50483 | 0.043291 | 1.0644 | 439.731 | 4.2623 | 1.8593 | 1.0565
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.48557 | 0.48841 | 0.044154 | 1.0058 | 439.731 | 4.2623 | 1.8593 | 1.0096
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.46289 | 0.46835 | 0.021365 | 1.0118 | 439.731 | 4.2623 | 1.8593 | 1.0305
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.45521 | 0.4538 | 0.046089 | 0.99689 | 439.731 | 4.2623 | 1.8593 | 0.97999
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.47825 | 0.47071 | 0.068162 | 0.98422 | 439.731 | 4.2623 | 1.8593 | 1.2921
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.69705 | 0.71953 | 0.042482 | 1.0323 | 661.113 | 1.5164 | 2.2028 | 1.1115
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.68908 | 0.68876 | 0.017479 | 0.99953 | 661.113 | 1.5164 | 2.2028 | 1.0744
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.70225 | 0.71189 | 0.027325 | 1.0137 | 661.113 | 1.5164 | 2.2028 | 1.0875
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.68835 | 0.69651 | 0.020043 | 1.0119 | 661.113 | 1.5164 | 2.2028 | 1.0312
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.52931 | 0.51407 | 0.078639 | 0.97121 | 483.283 | 6.971 | 2.4579 | 1.0751
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.49385 | 0.51314 | 0.018247 | 1.0391 | 483.283 | 6.971 | 2.4579 | 1.0366
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.49225 | 0.50592 | 0.015234 | 1.0278 | 483.283 | 6.971 | 2.4579 | 1.014
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.49777 | 0.49959 | 0.0089679 | 1.0037 | 483.283 | 6.971 | 2.4579 | 0.91833
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.80076 | 0.79458 | 0.0074751 | 0.99229 | 833.145 | 11.9278 | 3.2838 | 1.0007
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.80469 | 0.80536 | 0.0066774 | 1.0008 | 833.145 | 11.9278 | 3.2838 | 0.99984
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.80244 | 0.80375 | 0.0070148 | 1.0016 | 833.145 | 11.9278 | 3.2838 | 1.0037
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.80018 | 0.80137 | 0.0067157 | 1.0015 | 833.145 | 11.9278 | 3.2838 | 1.0327
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.58651 | 0.59434 | 0.0087751 | 1.0134 | 602.763 | 15.7651 | 2.4656 | 1.0301
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.58509 | 0.59026 | 0.010264 | 1.0088 | 602.763 | 15.7651 | 2.4656 | 1.0008
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.59383 | 0.59541 | 0.012646 | 1.0027 | 602.763 | 15.7651 | 2.4656 | 1.0201
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.58891 | 0.60605 | 0.014589 | 1.0291 | 602.763 | 15.7651 | 2.4656 | 1.0121
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row2+4_Gtotal
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70992 | 0.70324 | 0.010185 | 0.99059 | 812.9336 | 23.8604 | 1.8929 | 1.0285
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.71154 | 0.69879 | 0.0090892 | 0.98208 | 812.9336 | 23.8604 | 1.8929 | 1.0129
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.7048 | 0.69443 | 0.0092845 | 0.98529 | 812.9336 | 23.8604 | 1.8929 | 1.0685
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70621 | 0.69861 | 0.011915 | 0.98925 | 812.9336 | 23.8604 | 1.8929 | 1.0476
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.78386 | 0.77048 | 0.010607 | 0.98293 | 925.707 | 26.5529 | 1.9791 | 1.0292
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.78271 | 0.77511 | 0.014621 | 0.99029 | 925.707 | 26.5529 | 1.9791 | 1.0409
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.7838 | 0.76239 | 0.013716 | 0.97268 | 925.707 | 26.5529 | 1.9791 | 1.0424
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.78359 | 0.76583 | 0.012477 | 0.97733 | 925.707 | 26.5529 | 1.9791 | 1.0284
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.74037 | 0.73486 | 0.011998 | 0.99256 | 867.4298 | 26.4181 | 1.9858 | 1.0665
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.74434 | 0.72839 | 0.013204 | 0.97857 | 867.4298 | 26.4181 | 1.9858 | 1.0335
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.74586 | 0.72809 | 0.010611 | 0.97618 | 867.4298 | 26.4181 | 1.9858 | 1.0575
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.74685 | 0.72949 | 0.013739 | 0.97676 | 867.4298 | 26.4181 | 1.9858 | 1.0251
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.7478 | 0.72335 | 0.010701 | 0.96731 | 867.4298 | 26.4181 | 1.9858 | 1.028
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.74649 | 0.71971 | 0.011534 | 0.96413 | 850.8869 | 22.8476 | 1.999 | 0.99955
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.74721 | 0.7228 | 0.0094177 | 0.96733 | 850.8869 | 22.8476 | 1.999 | 1.0096
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.74823 | 0.73196 | 0.010387 | 0.97826 | 850.8869 | 22.8476 | 1.999 | 1.0124
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.74972 | 0.73561 | 0.01286 | 0.98117 | 850.8869 | 22.8476 | 1.999 | 1.064
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.67006 | 0.65251 | 0.010736 | 0.97381 | 728.0154 | 15.5948 | 2.1316 | 1.0526
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.67471 | 0.66261 | 0.01045 | 0.98207 | 728.0154 | 15.5948 | 2.1316 | 1.0716
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.67418 | 0.66428 | 0.010639 | 0.98532 | 728.0154 | 15.5948 | 2.1316 | 0.99834
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.67652 | 0.66601 | 0.012706 | 0.98448 | 728.0154 | 15.5948 | 2.1316 | 1.0079
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.53685 | 0.52817 | 0.016593 | 0.98383 | 558.6606 | 11.5591 | 2.3417 | 0.98299
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.53843 | 0.532 | 0.0076373 | 0.98807 | 558.6606 | 11.5591 | 2.3417 | 1.0434
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.53841 | 0.52926 | 0.0082526 | 0.983 | 558.6606 | 11.5591 | 2.3417 | 0.99082
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.54017 | 0.5308 | 0.007328 | 0.98266 | 558.6606 | 11.5591 | 2.3417 | 1.0492
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.54111 | 0.53121 | 0.0074665 | 0.98169 | 558.6606 | 11.5591 | 2.3417 | 1.0492
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.45611 | 0.4508 | 0.0070633 | 0.98836 | 462.0446 | 6.9313 | 2.5404 | 1.0088
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.45576 | 0.45123 | 0.0048563 | 0.99006 | 462.0446 | 6.9313 | 2.5404 | 0.98881
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.45762 | 0.45232 | 0.0046445 | 0.98843 | 462.0446 | 6.9313 | 2.5404 | 1.0157
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.45792 | 0.45559 | 0.0050519 | 0.99493 | 462.0446 | 6.9313 | 2.5404 | 1.0307
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.49793 | 0.48109 | 0.0060765 | 0.96616 | 500.0702 | 4.3421 | 1.8743 | 0.99099
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.4939 | 0.48062 | 0.0059133 | 0.97311 | 500.0702 | 4.3421 | 1.8743 | 1.0317
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.49487 | 0.48321 | 0.005936 | 0.97645 | 500.0702 | 4.3421 | 1.8743 | 1.0641
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.49141 | 0.49528 | 0.012154 | 1.0079 | 500.0702 | 4.3421 | 1.8743 | 0.99165
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.48688 | 0.4826 | 0.010119 | 0.99121 | 500.0702 | 4.3421 | 1.8743 | 1.1093
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.68796 | 0.6702 | 0.008835 | 0.97418 | 706.197 | 1.5766 | 2.3056 | 1.0599
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.69385 | 0.66833 | 0.0070436 | 0.96322 | 706.197 | 1.5766 | 2.3056 | 1.0547
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.6849 | 0.67946 | 0.0089541 | 0.99205 | 706.197 | 1.5766 | 2.3056 | 1.0913
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.69226 | 0.67998 | 0.0096237 | 0.98226 | 706.197 | 1.5766 | 2.3056 | 1.013
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.54931 | 0.5316 | 0.015085 | 0.96776 | 563.7501 | 7.0156 | 2.4178 | 1.016
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.54294 | 0.55082 | 0.011089 | 1.0145 | 563.7501 | 7.0156 | 2.4178 | 1.0876
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.53958 | 0.54705 | 0.01179 | 1.0138 | 563.7501 | 7.0156 | 2.4178 | 1.0178
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.54561 | 0.54082 | 0.0093709 | 0.99123 | 563.7501 | 7.0156 | 2.4178 | 0.95714
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.78827 | 0.77871 | 0.010302 | 0.98788 | 854.2772 | 11.7995 | 3.2424 | 1.0338
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.79138 | 0.78553 | 0.011428 | 0.99261 | 854.2772 | 11.7995 | 3.2424 | 1.0189
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.79282 | 0.78667 | 0.0092637 | 0.99225 | 854.2772 | 11.7995 | 3.2424 | 1.0195
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.78818 | 0.78212 | 0.011633 | 0.99232 | 854.2772 | 11.7995 | 3.2424 | 1.0061
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.59914 | 0.60083 | 0.011083 | 1.0028 | 648.787 | 15.6896 | 2.4603 | 1.0425
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.61094 | 0.60118 | 0.016327 | 0.98402 | 648.787 | 15.6896 | 2.4603 | 0.98233
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.60268 | 0.59449 | 0.01265 | 0.98642 | 648.787 | 15.6896 | 2.4603 | 0.9945
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.59631 | 0.60627 | 0.0087014 | 1.0167 | 648.787 | 15.6896 | 2.4603 | 1.007
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row2+4_Method4
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70992 | 0.71574 | 0.010202 | 1.0082 | 812.9336 | 23.8604 | 1.8929
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.71154 | 0.71499 | 0.0099794 | 1.0049 | 812.9336 | 23.8604 | 1.8929
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.7048 | 0.70885 | 0.0098621 | 1.0058 | 812.9336 | 23.8604 | 1.8929
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70621 | 0.70539 | 0.012207 | 0.99884 | 812.9336 | 23.8604 | 1.8929
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.78386 | 0.78747 | 0.011037 | 1.0046 | 925.707 | 26.5529 | 1.9791
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.78271 | 0.78867 | 0.014076 | 1.0076 | 925.707 | 26.5529 | 1.9791
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.7838 | 0.78329 | 0.013265 | 0.99934 | 925.707 | 26.5529 | 1.9791
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.78359 | 0.78456 | 0.011255 | 1.0012 | 925.707 | 26.5529 | 1.9791
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.74037 | 0.74621 | 0.012785 | 1.0079 | 867.4298 | 26.4181 | 1.9858
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.74434 | 0.74617 | 0.011954 | 1.0025 | 867.4298 | 26.4181 | 1.9858
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.74586 | 0.7462 | 0.010806 | 1.0005 | 867.4298 | 26.4181 | 1.9858
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.74685 | 0.74495 | 0.013739 | 0.99745 | 867.4298 | 26.4181 | 1.9858
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.7478 | 0.74197 | 0.011519 | 0.9922 | 867.4298 | 26.4181 | 1.9858
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.74649 | 0.7397 | 0.011583 | 0.9909 | 850.8869 | 22.8476 | 1.999
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.74721 | 0.74027 | 0.0096185 | 0.99071 | 850.8869 | 22.8476 | 1.999
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.74823 | 0.74328 | 0.010081 | 0.99338 | 850.8869 | 22.8476 | 1.999
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.74972 | 0.74565 | 0.012228 | 0.99457 | 850.8869 | 22.8476 | 1.999
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.67006 | 0.66374 | 0.012244 | 0.99057 | 728.0154 | 15.5948 | 2.1316
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.67471 | 0.67159 | 0.010845 | 0.99538 | 728.0154 | 15.5948 | 2.1316
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.67418 | 0.66973 | 0.011398 | 0.9934 | 728.0154 | 15.5948 | 2.1316
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.67644 | 0.67463 | 0.012581 | 0.99732 | 728.0154 | 15.5948 | 2.1316
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.53685 | 0.52633 | 0.015536 | 0.98041 | 558.6606 | 11.5591 | 2.3417
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.53843 | 0.53336 | 0.0078652 | 0.99059 | 558.6606 | 11.5591 | 2.3417
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.53841 | 0.53242 | 0.0080768 | 0.98886 | 558.6606 | 11.5591 | 2.3417
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.54017 | 0.53044 | 0.0072705 | 0.982 | 558.6606 | 11.5591 | 2.3417
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.54111 | 0.53019 | 0.0076026 | 0.97981 | 558.6606 | 11.5591 | 2.3417
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.45611 | 0.44919 | 0.0066286 | 0.98484 | 462.0446 | 6.9313 | 2.5404
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.45576 | 0.44942 | 0.0051582 | 0.98607 | 462.0446 | 6.9313 | 2.5404
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.45762 | 0.44992 | 0.0049016 | 0.98317 | 462.0446 | 6.9313 | 2.5404
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.45792 | 0.44958 | 0.0048338 | 0.98179 | 462.0446 | 6.9313 | 2.5404
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.49793 | 0.48574 | 0.0064634 | 0.97552 | 500.0702 | 4.3421 | 1.8743
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.4939 | 0.48564 | 0.0058081 | 0.98328 | 500.0702 | 4.3421 | 1.8743
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.49487 | 0.47938 | 0.0062872 | 0.96869 | 500.0702 | 4.3421 | 1.8743
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.49141 | 0.4905 | 0.012024 | 0.99815 | 500.0702 | 4.3421 | 1.8743
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.48688 | 0.48033 | 0.010777 | 0.98656 | 500.0702 | 4.3421 | 1.8743
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.68796 | 0.68357 | 0.0081339 | 0.99362 | 706.197 | 1.5766 | 2.3056
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.69385 | 0.68639 | 0.0072658 | 0.98926 | 706.197 | 1.5766 | 2.3056
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.6849 | 0.68469 | 0.008835 | 0.9997 | 706.197 | 1.5766 | 2.3056
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.69226 | 0.6844 | 0.009345 | 0.98865 | 706.197 | 1.5766 | 2.3056
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.54931 | 0.53334 | 0.015083 | 0.97093 | 563.7501 | 7.0156 | 2.4178
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.54294 | 0.54267 | 0.010984 | 0.99951 | 563.7501 | 7.0156 | 2.4178
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.53958 | 0.54961 | 0.012515 | 1.0186 | 563.7501 | 7.0156 | 2.4178
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.54561 | 0.5422 | 0.0089469 | 0.99376 | 563.7501 | 7.0156 | 2.4178
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.78827 | 0.78635 | 0.010087 | 0.99757 | 854.2772 | 11.7995 | 3.2424
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.79138 | 0.78862 | 0.011336 | 0.99651 | 854.2772 | 11.7995 | 3.2424
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.79282 | 0.79194 | 0.0085462 | 0.99889 | 854.2772 | 11.7995 | 3.2424
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.78818 | 0.78543 | 0.011624 | 0.99651 | 854.2772 | 11.7995 | 3.2424
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.59914 | 0.60036 | 0.011334 | 1.002 | 648.787 | 15.6896 | 2.4603
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.61094 | 0.60452 | 0.016213 | 0.9895 | 648.787 | 15.6896 | 2.4603
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.60268 | 0.59699 | 0.013141 | 0.99056 | 648.787 | 15.6896 | 2.4603
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.59631 | 0.59938 | 0.00798 | 1.0051 | 648.787 | 15.6896 | 2.4603
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row2+4_regressAlb
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.77811 | 0.77447 | 0.01012 | 0.99532 | 845.425 | 41.0718 | 0.20342
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.77899 | 0.78059 | 0.010797 | 1.0021 | 845.425 | 41.0718 | 0.20342
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.7791 | 0.78179 | 0.01556 | 1.0035 | 845.425 | 41.0718 | 0.20342
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.78065 | 0.78106 | 0.014684 | 1.0005 | 845.425 | 41.0718 | 0.20342
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.8167 | 0.821 | 0.010453 | 1.0053 | 905.682 | 44.4187 | 0.19402
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.81801 | 0.81104 | 0.017381 | 0.99148 | 905.682 | 44.4187 | 0.19402
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.81913 | 0.80343 | 0.014583 | 0.98083 | 905.682 | 44.4187 | 0.19402
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.81895 | 0.80113 | 0.011723 | 0.97824 | 905.682 | 44.4187 | 0.19402
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.78574 | 0.76313 | 0.013507 | 0.97122 | 848.588 | 42.6133 | 0.21309
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.77986 | 0.74578 | 0.012672 | 0.9563 | 848.588 | 42.6133 | 0.21309
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.77794 | 0.75331 | 0.011404 | 0.96834 | 848.588 | 42.6133 | 0.21309
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.77628 | 0.75621 | 0.0085921 | 0.97414 | 848.588 | 42.6133 | 0.21309
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.77932 | 0.76364 | 0.013625 | 0.97988 | 848.588 | 42.6133 | 0.21309
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.78307 | 0.77565 | 0.013555 | 0.99052 | 844.39 | 40.5706 | 0.21685
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.78552 | 0.78266 | 0.017183 | 0.99636 | 844.39 | 40.5706 | 0.21685
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.78532 | 0.7916 | 0.018534 | 1.008 | 844.39 | 40.5706 | 0.21685
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.7923 | 0.78811 | 0.020465 | 0.9947 | 844.39 | 40.5706 | 0.21685
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.7266 | 0.70018 | 0.020411 | 0.96364 | 735.537 | 28.7135 | 0.24176
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.72485 | 0.72506 | 0.017341 | 1.0003 | 735.537 | 28.7135 | 0.24176
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.7263 | 0.72952 | 0.01301 | 1.0044 | 735.537 | 28.7135 | 0.24176
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.72518 | 0.73075 | 0.024881 | 1.0077 | 735.537 | 28.7135 | 0.24176
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.55646 | 0.55601 | 0.022915 | 0.99919 | 549.883 | 21.5218 | 0.26232
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.5674 | 0.56962 | 0.017197 | 1.0039 | 549.883 | 21.5218 | 0.26232
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.56665 | 0.5666 | 0.017878 | 0.99991 | 549.883 | 21.5218 | 0.26232
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.55656 | 0.56206 | 0.026479 | 1.0099 | 549.883 | 21.5218 | 0.26232
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.55973 | 0.54987 | 0.023577 | 0.98238 | 549.883 | 21.5218 | 0.26232
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.5071 | 0.50578 | 0.0169 | 0.99739 | 479.558 | 16.3328 | 0.31188
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.51126 | 0.5102 | 0.017957 | 0.99793 | 479.558 | 16.3328 | 0.31188
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.50201 | 0.5019 | 0.020575 | 0.99979 | 479.558 | 16.3328 | 0.31188
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.50409 | 0.50592 | 0.018018 | 1.0036 | 479.558 | 16.3328 | 0.31188
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.53497 | 0.56342 | 0.024816 | 1.0532 | 491.782 | 15.241 | 0.43154
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.53002 | 0.52982 | 0.032893 | 0.99961 | 491.782 | 15.241 | 0.43154
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.53295 | 0.52683 | 0.01637 | 0.98852 | 491.782 | 15.241 | 0.43154
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.52149 | 0.53125 | 0.038093 | 1.0187 | 491.782 | 15.241 | 0.43154
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.53189 | 0.5259 | 0.037078 | 0.98875 | 491.782 | 15.241 | 0.43154
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.71621 | 0.71222 | 0.033916 | 0.99444 | 673 | 16.2853 | 0.42448
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.70764 | 0.70627 | 0.011779 | 0.99806 | 673 | 16.2853 | 0.42448
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.70678 | 0.6961 | 0.029828 | 0.98489 | 673 | 16.2853 | 0.42448
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.69969 | 0.68688 | 0.014078 | 0.98169 | 673 | 16.2853 | 0.42448
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.74529 | 0.76345 | 0.043178 | 1.0244 | 742.496 | 21.9596 | 0.2407
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.7444 | 0.73248 | 0.010395 | 0.98399 | 742.496 | 21.9596 | 0.2407
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.74737 | 0.70919 | 0.023598 | 0.94892 | 742.496 | 21.9596 | 0.2407
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.74732 | 0.71195 | 0.014314 | 0.95267 | 742.496 | 21.9596 | 0.2407
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.89882 | 0.87811 | 0.010021 | 0.97696 | 926.922 | 26.3998 | 0.21775
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.90281 | 0.89321 | 0.010136 | 0.98937 | 926.922 | 26.3998 | 0.21775
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.90303 | 0.90054 | 0.014415 | 0.99725 | 926.922 | 26.3998 | 0.21775
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.90161 | 0.90358 | 0.016885 | 1.0022 | 926.922 | 26.3998 | 0.21775
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.78226 | 0.7899 | 0.013481 | 1.0098 | 808.686 | 29.8225 | 0.19595
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.77711 | 0.78301 | 0.010919 | 1.0076 | 808.686 | 29.8225 | 0.19595
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.78352 | 0.78935 | 0.016007 | 1.0075 | 808.686 | 29.8225 | 0.19595
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.78091 | 0.79887 | 0.0059402 | 1.023 | 808.686 | 29.8225 | 0.19595
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row4_POA
DATE FROM ISO | Column1 | SAM_test | DAS_test | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.85563 | 0.84899 | 0.99225 | 953.383 | 27.1513 | 2.1859 | 1.0123
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.87331 | 0.86839 | 0.99436 | 985.699 | 28.5225 | 1.7445 | 1.0017
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.5939 | 0.59562 | 1.0029 | 625.265 | 24.4908 | 1.4935 | 1.0356
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.69944 | 0.69913 | 0.99956 | 731.83 | 19.7878 | 1.982 | 1.0074
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.8545 | 0.8489 | 0.99345 | 953.121 | 27.1033 | 2.021 | 1.0229
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.6543 | 0.65854 | 1.0065 | 694.711 | 24.3386 | 1.8036 | 1.0372
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.82731 | 0.82055 | 0.99183 | 926.189 | 29.2695 | 2.0548 | 1.007
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.85528 | 0.85134 | 0.99539 | 962.416 | 28.7444 | 2.0112 | 1.005
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.65694 | 0.66308 | 1.0093 | 705.164 | 25.3542 | 1.7347 | 1.0565
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.81843 | 0.81543 | 0.99633 | 906.856 | 27.4879 | 2.1133 | 1.0322
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.71244 | 0.71412 | 1.0024 | 766.456 | 25.2986 | 2.0873 | 1.0838
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.80912 | 0.80049 | 0.98933 | 891.38 | 26.0027 | 1.9509 | 1.036
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.61835 | 0.61726 | 0.99824 | 653.263 | 26.2787 | 1.9266 | 1.014
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.80155 | 0.79516 | 0.99203 | 870.368 | 26.5397 | 2.2701 | 0.99552
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.70565 | 0.70174 | 0.99446 | 754.351 | 25.6271 | 2.0715 | 1.0184
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.8089 | 0.80964 | 1.0009 | 860.962 | 20.3245 | 1.9662 | 1.0142
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.77623 | 0.76782 | 0.98917 | 826.465 | 23.2718 | 2.0258 | 1.0137
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.756 | 0.75415 | 0.99756 | 800.875 | 21.361 | 1.8642 | 1.0381
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.77303 | 0.77767 | 1.006 | 783.111 | 14.2858 | 3.4887 | 1.0496
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.73184 | 0.73864 | 1.0093 | 745.967 | 13.5817 | 1.9607 | 1.0184
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.68147 | 0.68664 | 1.0076 | 682.14 | 15.2975 | 3.1318 | 1.033
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.23486 | 0.22334 | 0.95093 | 202.503 | 8.1107 | 1.69 | 1.123
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.64979 | 0.66192 | 1.0187 | 633.833 | 10.6225 | 3.4558 | 1.0347
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.43127 | 0.43931 | 1.0186 | 413.53 | 13.5525 | 2.8453 | 0.97907
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.56036 | 0.56942 | 1.0162 | 549.883 | 12.8226 | 2.102 | 1.0382
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.56514 | 0.56991 | 1.0084 | 555.488 | 16.6824 | 2.725 | 1.0282
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.35254 | 0.36342 | 1.0308 | 330.105 | 6.6406 | 2.2736 | 0.96113
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.49823 | 0.51178 | 1.0272 | 472.333 | 8.2801 | 3.4977 | 0.98163
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.51939 | 0.53535 | 1.0307 | 503.499 | 10.1462 | 2.7683 | 1.0324
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.42016 | 0.43654 | 1.039 | 393.847 | 3.3355 | 1.7435 | 1.0623
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.26942 | 0.30489 | 1.1317 | 254.355 | 2.0547 | 2.6023 | 0.93538
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.41898 | 0.44038 | 1.0511 | 384.088 | 7.6453 | 2.1527 | 1.0212
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.34084 | 0.35519 | 1.0421 | 325.166 | 9.7473 | 2.2539 | 1.0326
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.61149 | 0.62732 | 1.0259 | 593.768 | 2.9387 | 1.2575 | 1.0283
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.34522 | 0.36111 | 1.046 | 331.624 | 5.1002 | 2.1055 | 1.0543
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.74491 | 0.76885 | 1.0321 | 675.164 | 1.3755 | 1.8942 | 1.0366
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.64858 | 0.65168 | 1.0048 | 619.986 | 7.7618 | 3.0658 | 1.0548
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.56289 | 0.58837 | 1.0453 | 545.191 | 4.4839 | 1.904 | 1.0554
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.80417 | 0.80316 | 0.99874 | 816.775 | 12.7572 | 2.1581 | 1.0171
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.45219 | 0.45154 | 0.99856 | 358.574 | -6.2966 | 2.0227 | 1.1517
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.76997 | 0.78353 | 1.0176 | 771.023 | 9.0135 | 1.7365 | 1.0354
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.7791 | 0.79901 | 1.0256 | 785.29 | 9.9359 | 3.7208 | 1.034
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.67692 | 0.68507 | 1.012 | 679.08 | 11.5905 | 2.4526 | 1.0651
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.91658 | 0.91028 | 0.99313 | 937.019 | 9.5144 | 4.2094 | 1.0425
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.884 | 0.89266 | 1.0098 | 892.419 | 9.1669 | 4.3109 | 1.0171
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.89649 | 0.89205 | 0.99504 | 950.748 | 17.2224 | 2.7561 | 1.0056
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.83665 | 0.83848 | 1.0022 | 872.442 | 15.045 | 2.5178 | 1.0571
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.57221 | 0.58968 | 1.0305 | 573.743 | 13.087 | 2.6041 | 1.0655
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.945 | 0.94086 | 0.99561 | 1015.94 | 19.1363 | 2.9847 | 1.0147
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.59244 | 0.59925 | 1.0115 | 602.763 | 19.7714 | 2.3204 | 1.0399
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.78246 | 0.80442 | 1.0281 | 820.828 | 16.1212 | 2.2133 | 1.0255
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row4_Gtotal
DATE FROM ISO | Column1 | SAM_test | DAS_test | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.86964 | 0.85414 | 0.98217 | 1013.4766 | 27.0735 | 2.1545 | 1.0126
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.88395 | 0.86851 | 0.98253 | 1046.6192 | 28.587 | 1.7931 | 1.0067
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.51289 | 0.50852 | 0.99147 | 564.2127 | 24.4261 | 1.5372 | 1.0598
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.62569 | 0.61884 | 0.98906 | 682.7142 | 19.7107 | 1.9944 | 0.98958
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.81181 | 0.79704 | 0.9818 | 939.8232 | 27.0774 | 2.1083 | 1.0235
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.51773 | 0.52158 | 1.0074 | 569.3726 | 23.9294 | 1.8115 | 0.96235
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.82421 | 0.80303 | 0.9743 | 960.4434 | 28.4698 | 1.9744 | 1.0335
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.85505 | 0.83626 | 0.97802 | 1004.5097 | 28.1303 | 1.8941 | 1.0082
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.71152 | 0.7008 | 0.98493 | 806.2689 | 24.9824 | 1.7272 | 1.0504
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.79352 | 0.78019 | 0.9832 | 915.867 | 27.8874 | 2.0656 | 1.0226
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.58391 | 0.57485 | 0.98447 | 643.3076 | 25.3502 | 2.0895 | 1.0527
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.8214 | 0.8025 | 0.97698 | 945.1638 | 26.2581 | 1.9048 | 1.0458
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.51654 | 0.5104 | 0.98812 | 568.1167 | 25.6358 | 1.8224 | 1.0284
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.81027 | 0.79416 | 0.98011 | 928.6032 | 26.9145 | 2.13 | 1.0033
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.60051 | 0.58939 | 0.98149 | 665.1493 | 25.4112 | 1.9449 | 1.0614
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.82017 | 0.80448 | 0.98087 | 910.8144 | 20.235 | 2.0341 | 1.0269
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.68582 | 0.67367 | 0.98228 | 749.3945 | 20.3419 | 1.9519 | 1.0529
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.76175 | 0.74892 | 0.98316 | 843.6694 | 21.9245 | 1.9396 | 1.061
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.69554 | 0.68945 | 0.99125 | 727.1839 | 13.0363 | 3.2168 | 1.0894
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.74327 | 0.73653 | 0.99093 | 789.5121 | 14.1304 | 2.3393 | 1.0067
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.67518 | 0.67101 | 0.99382 | 711.8415 | 15.4312 | 2.8557 | 1.028
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.19449 | 0.1985 | 1.0206 | 196.9264 | 7.2866 | 1.6689 | 1.1473
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.57151 | 0.57259 | 1.0019 | 581.8833 | 9.3771 | 2.8987 | 1.0728
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.44714 | 0.44643 | 0.99842 | 460.0659 | 13.0367 | 2.6158 | 1.0196
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.57504 | 0.57081 | 0.99265 | 591.7651 | 11.9128 | 2.0599 | 1.0534
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.54582 | 0.54236 | 0.99365 | 564.173 | 15.9887 | 2.7173 | 1.0702
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.38916 | 0.39474 | 1.0143 | 390.5462 | 6.5607 | 2.5301 | 0.98998
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.45964 | 0.46059 | 1.0021 | 463.5976 | 8.1954 | 3.0815 | 1.0441
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.54393 | 0.54359 | 0.99939 | 551.5015 | 10.5032 | 2.9114 | 1.0378
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.42329 | 0.43369 | 1.0246 | 422.4382 | 3.3504 | 1.7556 | 1.1546
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.44244 | 0.44275 | 1.0007 | 440.8326 | -0.24607 | 2.4609 | 0.96719
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.52272 | 0.51592 | 0.987 | 528.2856 | 6.94 | 1.9512 | 1.0683
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.35131 | 0.3576 | 1.0179 | 353.723 | 9.0522 | 1.8899 | 0.99353
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.53134 | 0.54411 | 1.024 | 536.7691 | 1.4458 | 1.4281 | 1.0186
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.65186 | 0.654 | 1.0033 | 666.4378 | 4.7533 | 1.8733 | 1.0169
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.78325 | 0.76638 | 0.97846 | 798.4656 | 0.21551 | 2.0295 | 1.0317
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.6297 | 0.62463 | 0.99195 | 639.754 | 6.8978 | 3.3199 | 1.0491
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.76973 | 0.76137 | 0.98913 | 790.0227 | 3.1817 | 1.7483 | 1.0135
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.84134 | 0.82945 | 0.98587 | 896.0006 | 10.0393 | 1.9524 | 1.0012
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.4177 | 0.43248 | 1.0354 | 419.4779 | -6.1985 | 2.2212 | 1.0185
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.64011 | 0.65293 | 1.02 | 668.0207 | 7.833 | 1.8396 | 1.075
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.49109 | 0.50773 | 1.0339 | 504.4582 | 8.1781 | 3.513 | 1.07
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.52441 | 0.52928 | 1.0093 | 545.8175 | 11.2969 | 2.3364 | 0.96852
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.86462 | 0.86306 | 0.9982 | 916.4965 | 9.1058 | 3.9246 | 1.1058
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.77437 | 0.77674 | 1.0031 | 804.5279 | 7.7841 | 3.9599 | 1.0333
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.87243 | 0.86379 | 0.9901 | 954.0574 | 16.1804 | 3.0238 | 1.0329
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.74996 | 0.74918 | 0.99896 | 802.8961 | 14.4498 | 2.8906 | 1.0143
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.38435 | 0.39983 | 1.0403 | 400.8909 | 11.7726 | 2.455 | 1.0868
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.93248 | 0.91935 | 0.98592 | 1038.9379 | 18.1367 | 2.8887 | 1.0236
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.36472 | 0.3683 | 1.0098 | 384.5305 | 16.899 | 1.9949 | 1.1464
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.55759 | 0.57844 | 1.0374 | 597.7102 | 15.6498 | 2.1813 | 1.0092
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## row4_Method3
DATE FROM ISO | Column1 | SAM_test | DAS_test | ratio | poa | t_amb | w_vel | IECratio
2022-01-16 15:30 | 2022-01-16 15:30:00-07:00 | 0.62307 | 0.53933 | 0.8656 | 641.889 | 9.628 | 2.0839 | 0.99504
2022-01-19 17:00 | 2022-01-19 17:00:00-07:00 | 0.60675 | 0.54864 | 0.90424 | 618.4239 | 5.3796 | 1.2279 | 0.98236
2022-01-23 08:15 | 2022-01-23 08:15:00-07:00 | 0.64577 | 0.57625 | 0.89235 | 655.688 | 3.1246 | 1.5222 | 0.99472
2022-01-26 09:30 | 2022-01-26 09:30:00-07:00 | 0.66008 | 0.57208 | 0.86668 | 671.3191 | 3.1064 | 1.668 | 1.0035
2022-01-29 08:45 | 2022-01-29 08:45:00-07:00 | 0.73608 | 0.64271 | 0.87315 | 764.5829 | 7.9341 | 1.6677 | 1.0096
2022-02-01 08:15 | 2022-02-01 08:15:00-07:00 | 0.74046 | 0.60624 | 0.81873 | 764.5829 | 4.9347 | 1.6622 | 0.96607
2022-02-04 07:45 | 2022-02-04 07:45:00-07:00 | 0.78333 | 0.62896 | 0.80293 | 798.4656 | 0.2361 | 1.7415 | 0.99333
2022-02-06 17:00 | 2022-02-06 17:00:00-07:00 | 0.74523 | 0.66193 | 0.88823 | 769.3049 | 7.065 | 2.5126 | 1.0292
2022-02-09 16:00 | 2022-02-09 16:00:00-07:00 | 0.70281 | 0.63024 | 0.89674 | 723.8256 | 8.3679 | 3.1306 | 1.0562
2022-02-12 17:45 | 2022-02-12 17:45:00-07:00 | 0.63634 | 0.56945 | 0.89489 | 654.1514 | 9.0781 | 2.8389 | 1.0503
2022-02-15 15:45 | 2022-02-15 15:45:00-07:00 | 0.82194 | 0.73003 | 0.88818 | 859.8448 | 7.7926 | 2.2224 | 1.0436
2022-02-18 14:30 | 2022-02-18 14:30:00-07:00 | 0.80763 | 0.72508 | 0.89778 | 845.6863 | 7.2911 | 1.7425 | 1.0523
2022-02-21 12:15 | 2022-02-21 12:15:00-07:00 | 0.77852 | 0.70906 | 0.91078 | 818.8303 | 8.7563 | 1.8214 | 1.0371
2022-02-27 09:30 | 2022-02-27 09:30:00-07:00 | 0.79711 | 0.72543 | 0.91007 | 846.5064 | 10.224 | 1.7586 | 1.0553
2022-03-02 07:30 | 2022-03-02 07:30:00-07:00 | 0.77493 | 0.71477 | 0.92237 | 842.1691 | 16.9836 | 1.9525 | 1.0184
2022-03-04 15:15 | 2022-03-04 15:15:00-07:00 | 0.72995 | 0.66181 | 0.90666 | 776.1974 | 13.3602 | 1.8812 | 1.0264
2022-03-09 07:30 | 2022-03-09 07:30:00-07:00 | 0.58473 | 0.54745 | 0.93624 | 585.8809 | -4.1408 | 1.8217 | 0.88657
2022-03-12 18:00 | 2022-03-12 18:00:00-07:00 | 0.8421 | 0.785 | 0.9322 | 894.8607 | 9.5309 | 2.7917 | 1.0712
2022-03-15 13:15 | 2022-03-15 13:15:00-07:00 | 0.82081 | 0.75899 | 0.92468 | 882.1314 | 10.3239 | 2.3621 | 1.1049
2022-03-18 08:00 | 2022-03-18 08:00:00-07:00 | 0.61339 | 0.56123 | 0.91496 | 643.0613 | 10.7868 | 2.1219 | 1.0455
2022-03-20 14:15 | 2022-03-20 14:15:00-07:00 | 0.52993 | 0.49794 | 0.93963 | 547.856 | 7.4801 | 2.6138 | 1.0605
2022-03-23 08:00 | 2022-03-23 08:00:00-07:00 | 0.61302 | 0.57856 | 0.94379 | 641.5406 | 9.8338 | 2.8857 | 0.97397
2022-03-25 14:00 | 2022-03-25 14:00:00-07:00 | 0.62607 | 0.58193 | 0.9295 | 665.3115 | 16.1019 | 3.0365 | 0.98784
2022-03-28 07:00 | 2022-03-28 07:00:00-07:00 | 0.62897 | 0.58106 | 0.92383 | 665.3115 | 14.3056 | 2.6473 | 0.99572
2022-03-30 13:00 | 2022-03-30 13:00:00-07:00 | 0.6721 | 0.62174 | 0.92508 | 709.9207 | 12.1512 | 2.3868 | 1.1038
2022-04-01 18:15 | 2022-04-01 18:15:00-07:00 | 0.57605 | 0.53709 | 0.93237 | 596.4984 | 8.8313 | 2.5787 | 0.95611
2022-04-04 10:30 | 2022-04-04 10:30:00-07:00 | 0.48893 | 0.45923 | 0.93925 | 503.3149 | 9.5073 | 3.2886 | 0.9548
2022-04-09 11:15 | 2022-04-09 11:15:00-07:00 | 0.65041 | 0.60321 | 0.92744 | 685.6246 | 13.8098 | 2.9792 | 1.1043
2022-04-11 15:15 | 2022-04-11 15:15:00-07:00 | 0.65845 | 0.61178 | 0.92912 | 693.3251 | 13.1455 | 3.3696 | 1.0795
2022-04-13 18:45 | 2022-04-13 18:45:00-07:00 | 0.5526 | 0.51544 | 0.93276 | 567.3975 | 8.7306 | 2.929 | 0.97967
2022-04-16 09:00 | 2022-04-16 09:00:00-07:00 | 0.55093 | 0.50896 | 0.92382 | 562.4252 | 8.0384 | 2.26 | 1.0487
2022-04-18 12:45 | 2022-04-18 12:45:00-07:00 | 0.56457 | 0.51841 | 0.91824 | 581.9311 | 11.0034 | 2.0826 | 1.057
2022-04-20 17:00 | 2022-04-20 17:00:00-07:00 | 0.7033 | 0.64833 | 0.92185 | 743.5358 | 14.8688 | 2.7529 | 1.1303
2022-04-23 07:30 | 2022-04-23 07:30:00-07:00 | 0.6541 | 0.60643 | 0.92712 | 686.2277 | 12.9632 | 2.6802 | 1.0568
2022-04-25 10:15 | 2022-04-25 10:15:00-07:00 | 0.64309 | 0.59642 | 0.92742 | 679.1601 | 13.9224 | 2.5667 | 1.0351
2022-04-27 13:45 | 2022-04-27 13:45:00-07:00 | 0.56423 | 0.52098 | 0.92334 | 593.9529 | 15.2701 | 2.3044 | 0.96867
2022-04-29 17:15 | 2022-04-29 17:15:00-07:00 | 0.55132 | 0.51221 | 0.92905 | 578.9108 | 14.3043 | 2.6434 | 0.98142
2022-05-02 06:15 | 2022-05-02 06:15:00-07:00 | 0.57165 | 0.5384 | 0.94184 | 593.9529 | 9.0286 | 2.7071 | 0.9941
2022-05-04 09:15 | 2022-05-04 09:15:00-07:00 | 0.54901 | 0.52174 | 0.95033 | 578.9108 | 13.5171 | 2.7558 | 1.018
2022-05-06 11:15 | 2022-05-06 11:15:00-07:00 | 0.57545 | 0.54405 | 0.94545 | 612.0051 | 16.2681 | 2.585 | 1.0078
2022-05-08 14:15 | 2022-05-08 14:15:00-07:00 | 0.65305 | 0.61252 | 0.93794 | 704.998 | 20.0271 | 2.7439 | 1.0415
2022-05-10 16:45 | 2022-05-10 16:45:00-07:00 | 0.68345 | 0.64137 | 0.93843 | 731.0545 | 16.4543 | 1.903 | 1.0243
2022-05-13 05:00 | 2022-05-13 05:00:00-07:00 | 0.68087 | 0.63621 | 0.9344 | 732.782 | 19.3602 | 1.8695 | 0.93164
2022-05-15 06:45 | 2022-05-15 06:45:00-07:00 | 0.43023 | 0.4086 | 0.94971 | 457.0895 | 21.3349 | 2.0148 | 1.032
2022-05-17 08:15 | 2022-05-17 08:15:00-07:00 | 0.54272 | 0.5073 | 0.93475 | 586.079 | 23.0165 | 2.4591 | 1.0446
2022-05-19 10:15 | 2022-05-19 10:15:00-07:00 | 0.54884 | 0.51051 | 0.93017 | 589.6322 | 20.2081 | 2.4653 | 1.0721
2022-05-21 11:45 | 2022-05-21 11:45:00-07:00 | 0.53243 | 0.5011 | 0.94115 | 561.2562 | 14.4538 | 2.3677 | 1.0576
2022-05-23 12:45 | 2022-05-23 12:45:00-07:00 | 0.45501 | 0.43955 | 0.96602 | 471.3218 | 10.5358 | 1.8945 | 1.062
2022-05-25 14:45 | 2022-05-25 14:45:00-07:00 | 0.4452 | 0.43316 | 0.97297 | 471.3218 | 16.7375 | 2.2311 | 1.0392
2022-05-27 16:45 | 2022-05-27 16:45:00-07:00 | 0.45379 | 0.43971 | 0.96898 | 484.3156 | 20.5874 | 2.3348 | 1.1025
2022-05-29 18:00 | 2022-05-29 18:00:00-07:00 | 0.41034 | 0.39622 | 0.96558 | 441.5012 | 22.0829 | 2.659 | 1.0252
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row4_Method4
DATE FROM ISO | Column1 | SAM_test | DAS_test | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.86939 | 0.86721 | 0.99749 | 1010.7954 | 27.0735 | 2.1545
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.88399 | 0.88494 | 1.0011 | 1044.0845 | 28.587 | 1.7931
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.56257 | 0.56571 | 1.0056 | 622.9246 | 24.4129 | 1.543
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.60189 | 0.6018 | 0.99983 | 652.7742 | 19.6965 | 1.9942
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.81171 | 0.81469 | 1.0037 | 937.1814 | 27.0774 | 2.1083
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.51893 | 0.52609 | 1.0138 | 568.8544 | 23.9294 | 1.8115
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.82419 | 0.81971 | 0.99456 | 958.112 | 28.4698 | 1.9744
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.85521 | 0.85542 | 1.0002 | 1002.3739 | 28.1303 | 1.8941
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.71141 | 0.71399 | 1.0036 | 804.0848 | 24.9824 | 1.7272
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.79326 | 0.79694 | 1.0046 | 913.715 | 27.8256 | 2.0179
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.58368 | 0.58551 | 1.0031 | 641.5297 | 25.3502 | 2.0895
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.82104 | 0.81931 | 0.99789 | 942.6656 | 26.2581 | 1.9048
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.51631 | 0.51829 | 1.0038 | 566.0451 | 25.6868 | 1.8224
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.81041 | 0.80769 | 0.99665 | 926.3379 | 26.9145 | 2.13
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.6005 | 0.59947 | 0.99829 | 663.3323 | 25.4112 | 1.9449
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.81951 | 0.81751 | 0.99755 | 907.9665 | 20.235 | 2.0341
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.67867 | 0.67492 | 0.99446 | 738.9057 | 20.4949 | 1.9779
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.76018 | 0.75753 | 0.99651 | 839.3979 | 21.8926 | 1.9338
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.729 | 0.72718 | 0.99751 | 762.8628 | 13.1934 | 3.314
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.74266 | 0.74024 | 0.99673 | 787.0399 | 14.2525 | 2.3215
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.67445 | 0.67528 | 1.0012 | 709.2213 | 15.4312 | 2.8557
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.21891 | 0.21982 | 1.0042 | 219.527 | 8.0203 | 1.675
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.61317 | 0.61373 | 1.0009 | 623.6776 | 9.2532 | 2.8425
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.47515 | 0.47407 | 0.99774 | 486.5642 | 12.732 | 2.5973
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.57341 | 0.56983 | 0.99376 | 589.4702 | 12.3203 | 1.9813
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.54787 | 0.54154 | 0.98845 | 564.7433 | 16.0498 | 2.7505
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.35723 | 0.36023 | 1.0084 | 356.8685 | 6.3415 | 2.5207
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.47614 | 0.47535 | 0.99833 | 479.4063 | 8.3804 | 3.0508
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.54281 | 0.54025 | 0.99528 | 549.0543 | 10.5745 | 2.926
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.42631 | 0.42834 | 1.0048 | 424.3939 | 3.5926 | 1.8187
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.43357 | 0.4349 | 1.0031 | 429.0147 | -0.55631 | 2.4739
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.53963 | 0.53626 | 0.99376 | 542.9895 | 7.224 | 1.9573
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.371 | 0.37045 | 0.99851 | 373.4063 | 9.0914 | 2.0191
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.49504 | 0.4988 | 1.0076 | 496.3897 | 1.3227 | 1.4436
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.6037 | 0.60729 | 1.0059 | 611.3674 | 4.508 | 1.9387
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.78387 | 0.78036 | 0.99553 | 790.9179 | -0.47814 | 1.9842
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.63531 | 0.63777 | 1.0039 | 642.1591 | 7.0797 | 3.3797
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.77203 | 0.77044 | 0.99794 | 789.0376 | 3.1817 | 1.7483
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.82964 | 0.82792 | 0.99792 | 880.5909 | 10.5711 | 2.0233
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.4285 | 0.44727 | 1.0438 | 425.5171 | -6.3271 | 2.1782
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.63661 | 0.63913 | 1.0039 | 660.136 | 8.2193 | 1.8024
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.49119 | 0.50626 | 1.0307 | 502.9568 | 8.1781 | 3.513
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.59045 | 0.59463 | 1.0071 | 616.5678 | 11.1081 | 2.3428
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.81076 | 0.82172 | 1.0135 | 853.5078 | 9.1749 | 3.8936
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.76813 | 0.77318 | 1.0066 | 795.3391 | 7.8773 | 3.9239
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.87807 | 0.88009 | 1.0023 | 960.3091 | 16.4878 | 3.0186
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.74994 | 0.75089 | 1.0013 | 801.0406 | 14.4498 | 2.8906
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.38433 | 0.39321 | 1.0231 | 399.2656 | 11.7726 | 2.455
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.93193 | 0.93203 | 1.0001 | 1036.7921 | 18.2934 | 2.8862
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.36575 | 0.37038 | 1.0126 | 383.1504 | 17.1383 | 1.9889
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.55769 | 0.57067 | 1.0233 | 595.7732 | 15.6498 | 2.1813
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## row4RefModvsRow8POA
DATE FROM ISO | Column1 | SAM_test | DAS_test | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.48768 | 0.50898 | 1.0437 | 552.504 | 25.7646 | 1.9987
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.55756 | 0.5808 | 1.0417 | 642.852 | 27.1709 | 1.4291
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.38109 | 0.39921 | 1.0476 | 429.676 | 24.0127 | 1.4426
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.58458 | 0.60261 | 1.0308 | 652.95 | 19.2816 | 1.8632
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.50577 | 0.53015 | 1.0482 | 574.977 | 25.9223 | 1.89
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.49248 | 0.51717 | 1.0501 | 559.916 | 24.5136 | 1.609
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.64674 | 0.66395 | 1.0266 | 751.727 | 27.5504 | 1.8625
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.55437 | 0.57771 | 1.0421 | 637.079 | 25.9952 | 1.6926
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.57084 | 0.5915 | 1.0362 | 657.165 | 26.0375 | 1.6924
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.62898 | 0.65334 | 1.0387 | 727.386 | 27.6284 | 2.1781
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.53631 | 0.56012 | 1.0444 | 610.862 | 25.4678 | 1.96
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.67772 | 0.70118 | 1.0346 | 783.398 | 25.6259 | 1.9064
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.53003 | 0.55422 | 1.0456 | 607.042 | 25.7731 | 1.9112
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.74635 | 0.76875 | 1.03 | 870.368 | 25.7778 | 2.1498
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.73405 | 0.75315 | 1.026 | 853.396 | 26.0841 | 2.2079
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.76871 | 0.79125 | 1.0293 | 874.46 | 20.5612 | 2.104
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.71573 | 0.73842 | 1.0317 | 825.429 | 24.5937 | 2.1921
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.70584 | 0.72807 | 1.0315 | 801.45 | 22.0386 | 2.0139
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.72525 | 0.74697 | 1.03 | 788.015 | 15.4477 | 3.8381
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.69317 | 0.71424 | 1.0304 | 761.634 | 15.6376 | 2.1315
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.6393 | 0.66131 | 1.0344 | 692.323 | 15.6963 | 3.1223
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.61437 | 0.63053 | 1.0263 | 669.299 | 15.8329 | 1.8752
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.59086 | 0.61164 | 1.0352 | 622.797 | 11.1039 | 3.4272
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.53141 | 0.54781 | 1.0309 | 563.789 | 12.6816 | 2.5665
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.53421 | 0.54968 | 1.029 | 571.23 | 14.4971 | 2.1123
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.50314 | 0.51703 | 1.0276 | 540.32 | 16.9277 | 2.5162
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.45205 | 0.46805 | 1.0354 | 469.5 | 8.0883 | 2.0415
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.47167 | 0.48709 | 1.0327 | 494.387 | 10.2458 | 1.9087
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.49241 | 0.50608 | 1.0278 | 514.093 | 10.7369 | 2.7296
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.4272 | 0.44051 | 1.0312 | 437.027 | 3.9647 | 1.7846
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.5165 | 0.53111 | 1.0283 | 531.436 | 4.4333 | 2.5827
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.52923 | 0.54456 | 1.029 | 553.212 | 8.0045 | 1.8818
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.50295 | 0.51712 | 1.0282 | 532.678 | 11.2304 | 2.0143
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.6006 | 0.61858 | 1.0299 | 623.52 | 3.3315 | 1.4721
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.62226 | 0.64186 | 1.0315 | 658.643 | 8.3125 | 1.8686
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.67271 | 0.6945 | 1.0324 | 704.415 | 3.2844 | 1.635
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.65014 | 0.67274 | 1.0348 | 685.493 | 9.2817 | 3.4265
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.72399 | 0.74727 | 1.0322 | 772.045 | 6.4355 | 1.6555
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.74922 | 0.77424 | 1.0334 | 816.775 | 10.3263 | 1.7111
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.81714 | 0.84906 | 1.0391 | 851.245 | -1.4419 | 1.8148
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.79445 | 0.81664 | 1.0279 | 867.449 | 10.1603 | 2.1429
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.76152 | 0.79629 | 1.0457 | 828.631 | 11.8321 | 3.4041
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.55208 | 0.57463 | 1.0408 | 595.374 | 12.3503 | 2.3421
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.41445 | 0.43512 | 1.0499 | 435.173 | 9.6247 | 3.4779
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.51937 | 0.54038 | 1.0405 | 541.819 | 8.1725 | 3.1979
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.65309 | 0.68113 | 1.0429 | 710.046 | 15.212 | 3.007
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.61687 | 0.63945 | 1.0366 | 675.387 | 15.1567 | 2.2096
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.55282 | 0.58015 | 1.0494 | 608.61 | 17.3799 | 2.9244
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.68838 | 0.71158 | 1.0337 | 769.563 | 19.5032 | 2.1344
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.59119 | 0.61557 | 1.0412 | 667.598 | 22.6519 | 2.463
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.42569 | 0.4508 | 1.059 | 466.976 | 17.3195 | 2.4082
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row2_POA
DATE FROM ISO | Column1 | SAM_test | DAS_test | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.80818 | 0.80538 | 0.99655 | 940.648 | 26.957 | 2.158 | 1.0141
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.8291 | 0.83053 | 1.0017 | 985.699 | 28.5571 | 1.7571 | 1.0137
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.57195 | 0.57029 | 0.9971 | 625.265 | 24.4908 | 1.4935 | 1.0278
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.65975 | 0.65121 | 0.98705 | 711.579 | 19.8219 | 2.0085 | 0.97369
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.81449 | 0.81237 | 0.9974 | 955.211 | 27.2922 | 1.9825 | 1.0308
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.63048 | 0.63034 | 0.99979 | 694.711 | 24.3386 | 1.8036 | 1.0208
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.78831 | 0.78405 | 0.99459 | 926.189 | 29.3574 | 2.0455 | 1.0303
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.8124 | 0.81084 | 0.99808 | 962.416 | 28.8272 | 1.9688 | 1.0058
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.63264 | 0.62943 | 0.99493 | 705.164 | 25.4191 | 1.7424 | 1.04
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.76893 | 0.76367 | 0.99316 | 889.804 | 27.7401 | 2.0782 | 1.0431
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.68585 | 0.67735 | 0.98761 | 766.456 | 25.376 | 2.0686 | 1.0616
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.77381 | 0.76096 | 0.98339 | 891.38 | 26.0627 | 1.9433 | 1.0161
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.59619 | 0.58491 | 0.98109 | 652.352 | 26.2019 | 1.9257 | 0.98858
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.76486 | 0.75311 | 0.98464 | 867.341 | 26.5621 | 2.1585 | 0.99374
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.68473 | 0.67202 | 0.98143 | 762.109 | 25.6816 | 2.0619 | 0.98867
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.77843 | 0.77035 | 0.98962 | 860.962 | 20.2871 | 2.0077 | 1.0113
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.74477 | 0.73337 | 0.98469 | 826.465 | 23.365 | 2.0409 | 1.0007
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.72769 | 0.72078 | 0.9905 | 801.45 | 21.4623 | 1.8792 | 1.0608
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.73654 | 0.72737 | 0.98755 | 763.012 | 14.3532 | 3.7496 | 1.0224
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.71361 | 0.70978 | 0.99464 | 746.85 | 13.2858 | 2.1147 | 0.99646
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.66082 | 0.65392 | 0.98955 | 678.029 | 14.9728 | 3.1484 | 1.0051
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.34321 | 0.35262 | 1.0274 | 344.164 | 8.0535 | 1.6941 | 1.0099
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.62793 | 0.62104 | 0.98903 | 622.797 | 9.9946 | 3.4374 | 1.0072
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.42369 | 0.41933 | 0.9897 | 413.53 | 13.5339 | 2.8128 | 0.96584
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.54808 | 0.54469 | 0.99382 | 549.883 | 12.8226 | 2.102 | 1.0121
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.53133 | 0.52229 | 0.98299 | 533.913 | 16.7034 | 2.8367 | 1.042
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.34862 | 0.34547 | 0.99098 | 330.105 | 6.5616 | 2.2299 | 0.92112
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.51207 | 0.50277 | 0.98184 | 494.387 | 8.011 | 3.5202 | 0.93209
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.51448 | 0.5046 | 0.9808 | 503.499 | 10.4729 | 2.9324 | 0.96955
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.41136 | 0.41081 | 0.99868 | 391.107 | 3.2625 | 1.7275 | 1.0214
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.28952 | 0.30889 | 1.0669 | 275.632 | 1.9504 | 2.6237 | 0.91234
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.41346 | 0.4164 | 1.0071 | 384.088 | 7.6945 | 2.1582 | 0.9569
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.27709 | 0.27813 | 1.0037 | 263.498 | 9.5873 | 2.1827 | 1.0145
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.59976 | 0.59934 | 0.9993 | 593.768 | 2.9387 | 1.2575 | 0.99879
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.43831 | 0.44352 | 1.0119 | 423.232 | 5.3048 | 2.1222 | 1.1933
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.72628 | 0.73216 | 1.0081 | 675.941 | 1.8101 | 1.939 | 1.0421
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.6347 | 0.6301 | 0.99276 | 621.544 | 7.806 | 3.0537 | 1.0413
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.52054 | 0.52584 | 1.0102 | 510.992 | 4.4342 | 1.8965 | 1.1198
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.77794 | 0.77135 | 0.99153 | 816.775 | 12.7572 | 2.1581 | 1.0124
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.43148 | 0.40649 | 0.94206 | 346.173 | -6.4084 | 2.1502 | 1.0053
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.8165 | 0.81631 | 0.99976 | 853.291 | 9.2933 | 1.7502 | 1.0201
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.75989 | 0.76339 | 1.0046 | 782.555 | 10.0452 | 3.7669 | 1.0211
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.65984 | 0.65451 | 0.99193 | 679.08 | 11.7018 | 2.4346 | 1.0437
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.89095 | 0.87665 | 0.98394 | 937.019 | 9.6924 | 4.0545 | 1.0221
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.86753 | 0.85781 | 0.98879 | 902.536 | 10.2734 | 4.3294 | 0.97894
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.86125 | 0.84786 | 0.98445 | 950.748 | 17.5738 | 2.6472 | 0.99868
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.79548 | 0.78606 | 0.98815 | 853.911 | 14.8327 | 2.637 | 1.0325
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.53054 | 0.53273 | 1.0041 | 541.277 | 13.0019 | 2.6399 | 0.9547
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.89668 | 0.88234 | 0.98401 | 999.776 | 18.9057 | 2.9703 | 0.99527
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.52322 | 0.51016 | 0.97504 | 539.312 | 19.6567 | 2.3399 | 1.0214
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.74882 | 0.75458 | 1.0077 | 811.821 | 16.2564 | 2.2325 | 1.0108
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row2_Gtotal
DATE FROM ISO | Column1 | SAM_test | DAS_test | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.82297 | 0.81104 | 0.98551 | 1001.7275 | 27.0142 | 2.1727 | 1.018
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.83809 | 0.82988 | 0.9902 | 1043.2927 | 28.6004 | 1.8013 | 1.0185
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.49573 | 0.48505 | 0.97847 | 562.647 | 24.348 | 1.5473 | 0.99144
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.60538 | 0.59384 | 0.98093 | 681.4334 | 19.7322 | 2.0109 | 1.004
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.77311 | 0.75845 | 0.98103 | 932.9849 | 26.9834 | 2.0847 | 1.0235
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.50225 | 0.50026 | 0.99605 | 569.0551 | 23.9624 | 1.8146 | 0.9406
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.78548 | 0.76741 | 0.97699 | 958.0962 | 28.4698 | 1.9744 | 1.0455
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.81374 | 0.79705 | 0.97949 | 1001.7961 | 28.2277 | 1.9523 | 1.0088
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.68241 | 0.66571 | 0.97553 | 804.3497 | 24.9141 | 1.6684 | 1.0513
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.7651 | 0.75022 | 0.98054 | 927.5159 | 28.0756 | 1.9206 | 1.0089
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.56516 | 0.54674 | 0.9674 | 642.3836 | 25.355 | 2.0978 | 1.0227
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.78176 | 0.75696 | 0.96827 | 937.3611 | 26.1598 | 1.9126 | 1.0333
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.51839 | 0.49916 | 0.96291 | 589.0418 | 25.6189 | 1.8308 | 0.99486
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.77419 | 0.75356 | 0.97336 | 926.3283 | 26.8844 | 2.0663 | 0.99417
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.63245 | 0.60705 | 0.95983 | 730.1656 | 25.5108 | 1.9586 | 1.0243
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.78815 | 0.76402 | 0.96939 | 908.1287 | 20.0894 | 2.0422 | 1.0117
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.66172 | 0.64503 | 0.97478 | 747.4417 | 20.5412 | 1.9676 | 1.054
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.73157 | 0.71138 | 0.9724 | 839.9519 | 21.9571 | 1.9311 | 1.0341
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.67681 | 0.65618 | 0.96953 | 725.2689 | 13.2496 | 3.1818 | 1.0813
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.7203 | 0.70159 | 0.97403 | 788.3787 | 14.3977 | 2.2847 | 0.98959
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.6595 | 0.64367 | 0.97599 | 712.326 | 15.1046 | 2.7507 | 1.0131
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.19957 | 0.19521 | 0.97815 | 203.0773 | 8.0697 | 1.6709 | 1.0793
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.60092 | 0.58392 | 0.97171 | 624.1875 | 9.2532 | 2.8425 | 1.0309
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.42873 | 0.41693 | 0.97249 | 446.9366 | 12.5753 | 2.4973 | 0.97296
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.5603 | 0.54266 | 0.96853 | 589.9367 | 12.1077 | 1.9431 | 1.0295
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.53336 | 0.51451 | 0.96466 | 563.4262 | 15.9887 | 2.7173 | 1.0271
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.35346 | 0.34201 | 0.96763 | 357.2971 | 6.741 | 2.5192 | 0.90267
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.46926 | 0.45381 | 0.96706 | 479.7851 | 8.2361 | 2.6924 | 0.97457
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.53155 | 0.5126 | 0.96434 | 548.8552 | 11.5001 | 2.9647 | 0.99617
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.42105 | 0.4113 | 0.97685 | 422.2428 | 3.3504 | 1.7556 | 1.0655
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.43009 | 0.41316 | 0.96064 | 429.1966 | -0.14561 | 2.4662 | 0.96051
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.52976 | 0.50347 | 0.95036 | 544.3769 | 7.3162 | 1.9747 | 1.0147
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.27678 | 0.27341 | 0.98783 | 281.6502 | 9.3014 | 1.9402 | 1.0072
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.59682 | 0.58421 | 0.97887 | 613.7265 | 1.8423 | 1.4671 | 0.9968
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.63987 | 0.61795 | 0.96574 | 664.783 | 4.7633 | 1.8852 | 0.98559
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.76335 | 0.72427 | 0.94879 | 792.2843 | 0.39595 | 2.0608 | 0.99212
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.61646 | 0.59501 | 0.96521 | 635.2846 | 6.7598 | 3.2639 | 0.99481
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.75152 | 0.72819 | 0.96896 | 790.9911 | 3.6243 | 1.7958 | 0.99181
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.79899 | 0.7801 | 0.97636 | 881.1329 | 10.8728 | 1.8978 | 1.0119
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.44939 | 0.42401 | 0.94353 | 451.6423 | -5.9996 | 2.1397 | 0.91928
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.62237 | 0.62011 | 0.99638 | 662.4182 | 8.0949 | 1.8066 | 1.0329
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.4776 | 0.47563 | 0.99587 | 494.6837 | 8.1882 | 3.5409 | 0.99408
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.51453 | 0.50497 | 0.98142 | 544.6735 | 11.3589 | 2.3391 | 0.97975
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.84253 | 0.8319 | 0.98738 | 916.8883 | 9.2345 | 3.7394 | 1.0948
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.75831 | 0.74025 | 0.97618 | 802.745 | 7.8742 | 3.9856 | 1.0004
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.85762 | 0.8379 | 0.97701 | 980.5107 | 17.3744 | 2.9255 | 1.0126
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.73599 | 0.72208 | 0.9811 | 813.4141 | 14.6386 | 2.7174 | 1.0135
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.37839 | 0.37899 | 1.0016 | 399.5947 | 12.0533 | 2.486 | 1.0448
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.89683 | 0.87243 | 0.9728 | 1036.6624 | 18.3413 | 2.8964 | 0.98811
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.35823 | 0.34581 | 0.96534 | 383.4822 | 16.8021 | 1.9766 | 1.0954
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.54351 | 0.54731 | 1.007 | 596.342 | 15.6498 | 2.1813 | 0.97157
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_00_row2_Method4
DATE FROM ISO | Column1 | SAM_test | DAS_test | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.82882 | 0.8324 | 1.0043 | 1012.271 | 27.1024 | 2.1387
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.83809 | 0.84557 | 1.0089 | 1043.2927 | 28.6004 | 1.8013
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.49573 | 0.48997 | 0.98839 | 562.647 | 24.348 | 1.5473
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.58369 | 0.57543 | 0.98586 | 653.2185 | 19.6555 | 1.9947
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.77311 | 0.77535 | 1.0029 | 932.9849 | 26.9834 | 2.0847
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.50225 | 0.5013 | 0.99811 | 569.0551 | 23.9624 | 1.8146
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.78548 | 0.78392 | 0.998 | 958.0962 | 28.4698 | 1.9744
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.81374 | 0.81474 | 1.0012 | 1001.7961 | 28.2277 | 1.9523
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.68241 | 0.67981 | 0.9962 | 804.3497 | 24.9141 | 1.6684
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.7651 | 0.76634 | 1.0016 | 927.5159 | 28.0756 | 1.9206
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.56516 | 0.55719 | 0.98589 | 642.3836 | 25.355 | 2.0978
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.78176 | 0.7753 | 0.99173 | 937.3611 | 26.1598 | 1.9126
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.51839 | 0.50862 | 0.98115 | 589.0418 | 25.6189 | 1.8308
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.77419 | 0.76731 | 0.99111 | 926.3283 | 26.8844 | 2.0663
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.63245 | 0.61979 | 0.97997 | 730.1656 | 25.5108 | 1.9586
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.78815 | 0.77714 | 0.98604 | 908.1287 | 20.0894 | 2.0422
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.66172 | 0.65046 | 0.98299 | 747.4417 | 20.5412 | 1.9676
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.73157 | 0.72205 | 0.98698 | 839.9519 | 21.9571 | 1.9311
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.67681 | 0.66326 | 0.97999 | 725.2689 | 13.2496 | 3.1818
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.7203 | 0.70963 | 0.98519 | 788.3787 | 14.3977 | 2.2847
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.6595 | 0.6511 | 0.98726 | 712.326 | 15.1046 | 2.7507
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.19957 | 0.19524 | 0.97831 | 203.0773 | 8.0697 | 1.6709
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.60092 | 0.5863 | 0.97566 | 624.1875 | 9.2532 | 2.8425
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.42873 | 0.41886 | 0.97698 | 446.9366 | 12.5753 | 2.4973
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.5603 | 0.54303 | 0.96918 | 589.9367 | 12.1077 | 1.9431
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.53336 | 0.51356 | 0.96287 | 563.4262 | 15.9887 | 2.7173
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.35346 | 0.34064 | 0.96373 | 357.2971 | 6.741 | 2.5192
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.46926 | 0.4509 | 0.96088 | 479.7851 | 8.2361 | 2.6924
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.53155 | 0.51078 | 0.96093 | 548.8552 | 11.5001 | 2.9647
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.42105 | 0.40608 | 0.96447 | 422.2428 | 3.3504 | 1.7556
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.43009 | 0.41567 | 0.96647 | 429.1966 | -0.14561 | 2.4662
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.52976 | 0.50943 | 0.96161 | 544.3769 | 7.3162 | 1.9747
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.27678 | 0.2688 | 0.97116 | 281.6502 | 9.3014 | 1.9402
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.59682 | 0.58156 | 0.97444 | 613.7265 | 1.8423 | 1.4671
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.63987 | 0.62299 | 0.97361 | 664.783 | 4.7633 | 1.8852
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.76335 | 0.74267 | 0.97291 | 792.2843 | 0.39595 | 2.0608
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.61646 | 0.60048 | 0.97407 | 635.2846 | 6.7598 | 3.2639
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.75152 | 0.7365 | 0.98002 | 790.9911 | 3.6243 | 1.7958
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.79899 | 0.79002 | 0.98877 | 881.1329 | 10.8728 | 1.8978
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.44939 | 0.43678 | 0.97193 | 451.6423 | -5.9996 | 2.1397
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.62237 | 0.61054 | 0.981 | 662.4182 | 8.0949 | 1.8066
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.4776 | 0.47421 | 0.99291 | 494.6837 | 8.1882 | 3.5409
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.51453 | 0.50567 | 0.98277 | 544.6735 | 11.3589 | 2.3391
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.84253 | 0.84148 | 0.99876 | 916.8883 | 9.2345 | 3.7394
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.75831 | 0.74692 | 0.98498 | 802.745 | 7.8742 | 3.9856
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.85762 | 0.85052 | 0.99172 | 980.5107 | 17.3744 | 2.9255
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.73599 | 0.72402 | 0.98374 | 813.4141 | 14.6386 | 2.7174
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.37839 | 0.37499 | 0.99102 | 399.5947 | 12.0533 | 2.486
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.89683 | 0.88619 | 0.98814 | 1036.6624 | 18.3413 | 2.8964
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.35823 | 0.34919 | 0.97477 | 383.4822 | 16.8021 | 1.9766
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.54351 | 0.54122 | 0.99579 | 596.342 | 15.6498 | 2.1813
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## row2RefMod_vRow8POA
DATE FROM ISO | Column1 | SAM_test | DAS_test | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.48768 | 0.48832 | 1.0013 | 552.504 | 25.7646 | 1.9987
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.55756 | 0.56047 | 1.0052 | 642.852 | 27.1709 | 1.4291
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.38109 | 0.38026 | 0.99783 | 429.676 | 24.0127 | 1.4426
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.58458 | 0.57612 | 0.98552 | 652.95 | 19.2816 | 1.8632
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.50577 | 0.5079 | 1.0042 | 574.977 | 25.9223 | 1.89
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.49248 | 0.4926 | 1.0002 | 559.916 | 24.5136 | 1.609
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.64674 | 0.63767 | 0.98597 | 751.727 | 27.5504 | 1.8625
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.55437 | 0.55078 | 0.99353 | 637.079 | 25.9952 | 1.6926
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.57084 | 0.56424 | 0.98844 | 657.165 | 26.0375 | 1.6924
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.62898 | 0.62328 | 0.99094 | 727.386 | 27.6284 | 2.1781
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.53631 | 0.53367 | 0.99507 | 610.862 | 25.4678 | 1.96
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.67772 | 0.66838 | 0.98621 | 783.398 | 25.6259 | 1.9064
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.53003 | 0.5261 | 0.99259 | 607.042 | 25.7731 | 1.9112
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.74635 | 0.73273 | 0.98175 | 870.368 | 25.7778 | 2.1498
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.73405 | 0.71478 | 0.97375 | 853.396 | 26.0841 | 2.2079
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.76871 | 0.75179 | 0.97799 | 874.46 | 20.5612 | 2.104
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.71573 | 0.70426 | 0.98397 | 825.429 | 24.5937 | 2.1921
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.70584 | 0.69361 | 0.98267 | 801.45 | 22.0386 | 2.0139
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.72525 | 0.71439 | 0.98502 | 788.015 | 15.4477 | 3.8381
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.69317 | 0.68419 | 0.98705 | 761.634 | 15.6376 | 2.1315
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.6393 | 0.63586 | 0.99463 | 692.323 | 15.6963 | 3.1223
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.61437 | 0.60419 | 0.98343 | 669.299 | 15.8329 | 1.8752
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.59086 | 0.58468 | 0.98954 | 622.797 | 11.1039 | 3.4272
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.53141 | 0.52298 | 0.98414 | 563.789 | 12.6816 | 2.5665
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.53421 | 0.52486 | 0.98251 | 571.23 | 14.4971 | 2.1123
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.50314 | 0.49151 | 0.97688 | 540.32 | 16.9277 | 2.5162
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.45205 | 0.44255 | 0.97898 | 469.5 | 8.0883 | 2.0415
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.47167 | 0.4611 | 0.97758 | 494.387 | 10.2458 | 1.9087
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.49241 | 0.48112 | 0.97707 | 514.093 | 10.7369 | 2.7296
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.4272 | 0.41937 | 0.98169 | 437.027 | 3.9647 | 1.7846
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.5165 | 0.50326 | 0.97436 | 531.436 | 4.4333 | 2.5827
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.52923 | 0.517 | 0.97691 | 553.212 | 8.0045 | 1.8818
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.50295 | 0.49332 | 0.98084 | 532.678 | 11.2304 | 2.0143
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.6006 | 0.59097 | 0.98397 | 623.52 | 3.3315 | 1.4721
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.62226 | 0.61289 | 0.98494 | 658.643 | 8.3125 | 1.8686
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.67271 | 0.66334 | 0.98607 | 704.415 | 3.2844 | 1.635
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.65014 | 0.64315 | 0.98925 | 685.493 | 9.2817 | 3.4265
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.72399 | 0.71708 | 0.99045 | 772.045 | 6.4355 | 1.6555
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.74922 | 0.74304 | 0.99175 | 816.775 | 10.3263 | 1.7111
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.81714 | 0.78635 | 0.96233 | 851.245 | -1.4419 | 1.8148
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.79445 | 0.78135 | 0.98352 | 867.449 | 10.1603 | 2.1429
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.76152 | 0.76153 | 1 | 828.631 | 11.8321 | 3.4041
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.55208 | 0.54904 | 0.99449 | 595.374 | 12.3503 | 2.3421
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.41445 | 0.41289 | 0.99624 | 435.173 | 9.6247 | 3.4779
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.51937 | 0.51458 | 0.99078 | 541.819 | 8.1725 | 3.1979
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.65309 | 0.64968 | 0.99478 | 710.046 | 15.212 | 3.007
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.61687 | 0.61002 | 0.9889 | 675.387 | 15.1567 | 2.2096
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.55282 | 0.55208 | 0.99865 | 608.61 | 17.3799 | 2.9244
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.68838 | 0.67888 | 0.9862 | 769.563 | 19.5032 | 2.1344
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.59119 | 0.58253 | 0.98535 | 667.598 | 22.6519 | 2.463
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.42569 | 0.42752 | 1.0043 | 466.976 | 17.3195 | 2.4082
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)