## Figures
SAMTMY2020 model results - Row 2+4 | [7 empty] | SAMTMYA01 model results - Row 2+4
Row | Method | ASTM / IEC | MBE | RMSE | MAX | MIN |  | Row | Method | ASTM / IEC | MBE | RMSE | MIN | MAX |  | NEW Refmod is 2.3% lower than Gtotal based on back covered field comparison. |  | OLD Refmod is 3.5% higher than Gtotal based on Spire point
8 | Tamb | ASTM | -0.01 | 1.32 | 1.0261 | 0.97066 | <- Mono baseline | 8 | Tamb | ASTM | -0.02 | 1.31 |  |  | <- Mono baseline
8 | Tmod | ASTM | 0.65 | 1.64 |  |  |  | 8 | Tmod | ASTM | 0.63 | 1.63
2+4 | POA | ASTM | 1.26 | 2.58 | 1.0926 | 0.94613 | <- Bifacial baseline ? | 2+4 | POA | ASTM | 0.96 | 2.32 | 0.95472 | 1.095 | <- Method 1 albedo only
2+4 | Gtotal | ASTM | -1.59 | 1.27 | 1.01 | 0.95223 | <- Method 2 | 2+4 | Gtotal | ASTM | -1.56 | 1.32 |  |  | <- Method 2
2+4 | Method4 | ASTM | -0.8 | 0.89 | 1.0201 | 0.97512 | <- Method 4 | 2+4 | Method4 | ASTM | -0.77 | 0.88 |  |  | <- Method 4
2+4 | Method4Min | ASTM | 0.88 | 1.32 |  |  | <- Method 4_min
2+4 | Method4Tcorr | ASTM | -0.3 | 1.32 | 1.0184 | 0.966 | <- Method 4_tcorr
SAM_IEC
[7 empty] | ` | Row | Method | ASTM / IEC | MBE | RMSE | MIN | MAX
[8 empty] | 8 | Tamb GHI | IEC | 0 | 1.2 | 0.96 | 1.03 | <- Mono 1b
Method 1 results with site-measured albedo and GHI/DHI field measurements | [7 empty] | 8 | Tamb POA | IEC | 1.6 | 0.9 | 1 | 1.04 | <- Mono 2
SAMS02 DHI+GHI Perez | [7 empty] | 2+4 | GHI+DHI | IEC | 0.7 | 0.9 | 0.99 | 1.02 | <- Method 1b
[8 empty] | 2+4 | Refcell | IEC | -1.1 | 0.9 | 0.97 | 1.01 | <- Method 2a
Row | Method | ASTM / IEC | MBE | RMSE | MAX | MIN |  | 2+4 | Refmod | IEC |  |  |  |  | <- Method 2b
8 | Tamb | ASTM | 0 | 1.13 | 1.034 | 0.9805 | <- Mono baseline | 2+4 | Refmod_tcorr | IEC | 0.9 | 0.8 | 1 | 1.03 | <- Method 2b_tcorr
2+4 | POA | ASTM | 0.57 | 1.5 | 1.0631 | 0.9826 | <- Method 1b
SAMP07 (CM11 POA and high freq albedo) - row 2+4
[8 empty] | Row | Method | ASTM / IEC | MBE | RMSE
[8 empty] | 8 | Tamb | ASTM | 0.01 | 1.76 | <- Mono baseline
[8 empty] | 8 | Tmod | ASTM | 0.9 | 1.99
[8 empty] | 2+4 | POA | ASTM | 0.43 | 2.84 | <- Method 1
[8 empty] | 2+4 | Gtotal | ASTM | -1.33 | 1.6 | <- Method 2
[8 empty] | 2+4 | Method4 | ASTM | -0.58 | 0.93 | <- Method 4
[8 empty] | 2+4 | Method4Min | ASTM | 1.03 | 1.83 | <- Method 4_min |  |  | Method4_calibration_3_29_2023.ipynb
SAMP00 (RefCell POA, high frequency albedo)
[8 empty] | Row | Method | ASTM / IEC | MBE | RMSE
[8 empty] | 8 | Tamb | ASTM | 0 | 1.68 | <- Mono baseline
[8 empty] | 8 | Tmod | ASTM | 0.91 | 1.88
[8 empty] | 2+4 | POA | ASTM | 0.46 | 2.49 | <- Method 1
[8 empty] | 2+4 | Gtotal | ASTM | -1.31 | 1.66 | <- Method 2
[8 empty] | 2+4 | Method4 | ASTM | -0.57 | 1.26 | <- Method 4
ROW 2+4 TMY2020
IEC
FILTERING COMPARISON - IEC

## IEC_7d
|  | ppi_2Mono | ppi_1BMono | ppi_1B | ppi_2A | ppi_2B | ppi_2B_tcorr | Gfront_poa | Grear | row2wind_speed | temp_ambient_FieldAverage | albedo_down | albedo_up | SRRL_DHI | Hydra_avg | power_dc_inv2 | row2tmod_1 | row2tmod_2 | power_dc_inv4 | row4tmod_1 | row4tmod_2 | power_dc_inv8 | row8tmod_1 | row8tmod_2 | power_dc_inv2+4 | power_dc_inv2+4_1B | power_dc_inv8_1B | Gfront_poa_1B | Grear_1B | power_dc_inv8_2Mono | Gfront_poa_2Mono | power_dc_inv8_2A | Gfront_poa_2A | Grear_2A | power_dc_inv8_2B | Gfront_poa_2B | Grear_2B | albedo_actual
2021-06-08 | 2021-06-08 00:00:00+00:00 | 1.0172 | 1.0076 | 1.0159 | 0.99103 | 1.0092 | 1.0203 | 719212.2071 | 53607.6348 | 1262.8157 | 19419.0519 | 101608.2644 | 557475.203 | 116316.3914 | 7105.6641 | 620.1926 | 38140.3156 | 38791.8077 | 645.4214 | 38024.4061 | 39047.2451 | 604.1314 | 39027.5205 | 39199.9604 | 632.807 | 622.8829 | 599.5634 | 712302.842 | 38232.7081 | 593.9023 | 714276.155 | 638.5348 | 752924.344 | 41351.2267 | 627.0361 | 738363.219 | 41053.9307 | 0.18227
2021-06-15 | 2021-06-15 00:00:00+00:00 | 1.0151 | 0.9947 | 0.99974 | 0.98387 | 1.0045 | 1.0169 | 837908.6254 | 67403.1616 | 1468.4875 | 23469.01 | 134460.3057 | 659750.2714 | 105727.8187 | 8288.5896 | 713.3877 | 45704.9969 | 46126.1676 | 746.4331 | 45505.6428 | 46328.6102 | 697.5873 | 46085.8864 | 46307.2976 | 729.9104 | 730.0986 | 701.304 | 840336.216 | 49462.6406 | 687.2108 | 832805.669 | 741.8783 | 881656.983 | 52594.4595 | 726.6684 | 862167.149 | 52044.3224 | 0.2038
2021-06-22 | 2021-06-22 00:00:00+00:00 | 1.023 | 1.0017 | 1.0047 | 0.99258 | 1.0146 | 1.0274 | 534099.5907 | 50757.8148 | 1093.114 | 18918.0175 | 95050.4682 | 438592.8533 | 148092.5321 | 5332.2753 | 459.1287 | 32640.7957 | 32985.4909 | 479.604 | 32826.3937 | 33338.3037 | 443.2563 | 33215.551 | 33424.4533 | 469.3664 | 467.1881 | 442.5064 | 532067.124 | 38097.3327 | 433.3071 | 528929.628 | 472.8732 | 565868.553 | 40041.1329 | 462.6052 | 552894.671 | 39681.5793 | 0.21672
2021-06-29 | 2021-06-29 00:00:00+00:00 | 1.0184 | 0.99768 | 1.0115 | 0.99571 | 1.0139 | 1.0228 | 370726.49 | 36811.9351 | 708.3345 | 10225.1972 | 62711.1159 | 313603.3658 | 133327.1262 | 3722.9053 | 330.0208 | 20027.4602 | 20317.1908 | 343.5092 | 20118.3995 | 20629.0505 | 315.3718 | 20483.2655 | 20657.6945 | 336.765 | 332.9379 | 316.1059 | 370283.546 | 26325.7451 | 309.6646 | 366745.961 | 338.2164 | 393134.355 | 27237.2845 | 332.1532 | 385382.486 | 26904.3912 | 0.19997
2021-07-06 | 2021-07-06 00:00:00+00:00 | 0.96321 | 0.96642 | 1.0238 | 0.98408 | 1.0047 | 1.0163 | 584936.4734 | 49635.7151 | 978.6535 | 16024.9973 | 87872.7771 | 454108.2465 | 113807.7111 | 5805.417 | 503.6384 | 31977.7147 | 32446.3839 | 525.196 | 31987.5531 | 32754.0525 | 465.3485 | 32708.0604 | 32895.0903 | 514.4172 | 502.4488 | 481.5202 | 571464.572 | 33650.0719 | 483.1239 | 580432.187 | 522.7412 | 616257.013 | 37298.4593 | 511.9994 | 602898.623 | 36868.3884 | 0.19351
2021-07-13 | 2021-07-13 00:00:00+00:00 | 1.0151 | 0.99296 | 1.0011 | 0.98652 | 1.0068 | 1.0192 | 608296.2204 | 54526.2874 | 1134.756 | 19431.6101 | 97299.5841 | 493553.1372 | 127300.8828 | 6060.129 | 520.2015 | 35971.1318 | 36044.5598 | 542.9823 | 35988.8934 | 36416.6681 | 503.1109 | 36275.1734 | 36464.8722 | 531.5919 | 531.0275 | 506.6793 | 607725.611 | 37937.0191 | 495.6334 | 603151.099 | 538.8583 | 642983.789 | 40864.5961 | 527.9839 | 629189.56 | 40553.3775 | 0.19714
2021-07-20 | 2021-07-20 00:00:00+00:00 | 1.0206 | 1.0014 | 1.0094 | 0.99152 | 1.0124 | 1.0248 | 567118.824 | 50006.7784 | 1091.816 | 17977.1248 | 88342.3615 | 453159.2654 | 125558.7007 | 5642.0569 | 487.8483 | 33180.8873 | 33261.8301 | 510.4335 | 33222.2527 | 33687.9299 | 472.859 | 33576.2521 | 33860.3041 | 499.1409 | 494.4951 | 472.1864 | 564785.612 | 34465.7283 | 463.3094 | 562411.782 | 503.411 | 598969.183 | 36880.651 | 493.0036 | 585912.747 | 36667.1332 | 0.19495
2021-07-27 | 2021-07-27 00:00:00+00:00 | 1.0165 | 1.0125 | 1.0192 | 0.98705 | 1.0087 | 1.0217 | 608548.3014 | 55241.6331 | 1199.762 | 20579.3321 | 95542.2677 | 500833.1972 | 150164.3488 | 6060.0196 | 519.0127 | 36853.1003 | 36891.4612 | 543.46 | 36890.7221 | 37414.6882 | 502.5623 | 37203.0013 | 37572.7518 | 531.2364 | 521.249 | 496.3653 | 597729.585 | 38348.6954 | 494.4122 | 603351.083 | 538.2074 | 643655.282 | 40716.8542 | 526.6494 | 629129.436 | 40377.9823 | 0.19077
2021-08-03 | 2021-08-03 00:00:00+00:00 | 1.0156 | 1.0105 | 1.0181 | 0.98622 | 1.0073 | 1.0194 | 573680.4874 | 52617.9619 | 1110.773 | 18489.4861 | 87960.9931 | 476260.6242 | 147961.5175 | 5719.6562 | 491.9357 | 34327.8683 | 34517.3881 | 516.1654 | 34141.4553 | 34849.5595 | 476.1026 | 34572.5602 | 34976.9707 | 504.0506 | 495.0941 | 471.1567 | 563350.036 | 35957.5774 | 468.8108 | 568749.498 | 511.0931 | 607162.049 | 37899.6035 | 500.4219 | 593812.164 | 37629.3002 | 0.18469
2021-08-10 | 2021-08-10 00:00:00+00:00 | 1.0312 | 1.0073 | 1.0122 | 1.0004 | 1.02 | 1.0309 | 548758.6867 | 51544.9734 | 1353.5715 | 19416.6129 | 81922.8903 | 455411.0546 | 187066.8835 | 5491.7977 | 480.5855 | 32670.9988 | 33561.7816 | 504.6716 | 33317.197 | 34006.4264 | 465.1309 | 33657.3411 | 33934.8703 | 492.6285 | 486.7097 | 461.7415 | 546296.394 | 34948.0065 | 451.0406 | 543067.85 | 492.4189 | 580684.723 | 36392.6028 | 482.9655 | 569173.305 | 36214.4789 | 0.17989
2021-08-17 | 2021-08-17 00:00:00+00:00 | 1.0207 | 1.0054 | 1.0108 | 0.98946 | 1.0115 | 1.0231 | 628928.4199 | 55989.0984 | 1386.1178 | 21203.9665 | 91774.5447 | 503771.7028 | 151076.0688 | 6255.5147 | 543.1858 | 36637.3539 | 37627.612 | 571.2942 | 37293.1355 | 38027.4373 | 528.2732 | 37718.5065 | 38060.4329 | 557.24 | 551.2611 | 525.4394 | 622895.769 | 37288.9558 | 517.5782 | 623783.233 | 563.1753 | 664810.781 | 39409.5283 | 550.89 | 649763.662 | 39183.7692 | 0.18217
2021-08-24 | 2021-08-24 00:00:00+00:00 | 1.0053 | 1.0048 | 1.0104 | 0.97336 | 0.99948 | 1.01 | 575889.0707 | 48863.1867 | 1327.02 | 16811.2004 | 80830.4313 | 444772.7265 | 106404.0202 | 5683.3073 | 494.6575 | 30429.2042 | 31280.3148 | 520.8925 | 31087.3843 | 31705.0349 | 484.0042 | 31310.7539 | 31589.1877 | 507.775 | 502.5461 | 481.6831 | 564210.972 | 31278.4675 | 481.4459 | 571850.939 | 521.6734 | 607241.839 | 33731.024 | 508.0413 | 590636.921 | 33345.0551 | 0.18173
2021-08-31 | 2021-08-31 00:00:00+00:00 | 1.0008 | 0.99777 | 1.0044 | 0.97035 | 0.99676 | 1.0083 | 617397.4124 | 52809.4083 | 1277.3105 | 19196.4052 | 90012.1789 | 459860.3546 | 98650.5916 | 6091.834 | 524.3474 | 34332.3749 | 35523.5344 | 553.5165 | 35101.3875 | 35912.4923 | 512.7981 | 35512.062 | 35813.3565 | 538.932 | 536.5721 | 513.946 | 606139.017 | 33630.2554 | 512.3977 | 613255.476 | 555.3989 | 651444.219 | 36667.6966 | 540.685 | 633221.822 | 36266.4801 | 0.19574
2021-09-07 | 2021-09-07 00:00:00+00:00 | 1.01 | 1.0048 | 1.0077 | 0.97681 | 1.0006 | 1.011 | 524131.8177 | 48832.2318 | 1360.0275 | 17155.8097 | 84303.3109 | 393175.6486 | 113788.8914 | 5215.9239 | 454.1888 | 29519.8961 | 30422.4216 | 480.121 | 30102.1942 | 30627.7127 | 442.9338 | 30219.1284 | 30381.9142 | 467.1549 | 463.5822 | 440.832 | 514717.878 | 32549.9509 | 438.5382 | 520192.27 | 478.2471 | 555672.648 | 34351.5612 | 466.8934 | 541920.977 | 34044.052 | 0.21442
2021-09-14 | 2021-09-14 00:00:00+00:00 | 1.0152 | 0.99847 | 1.0008 | 0.98061 | 1.0021 | 1.0133 | 572750.9609 | 54994.0841 | 1262.4385 | 19716.3028 | 95892.153 | 440762.3518 | 116438.2774 | 5726.458 | 495.4592 | 33885.4107 | 35013.7996 | 523.8284 | 34491.5039 | 35163.4739 | 482.4048 | 34706.6333 | 34956.1363 | 509.6438 | 509.2336 | 483.1427 | 568871.246 | 37110.9406 | 475.1988 | 568370.541 | 519.7197 | 608269.588 | 39495.4288 | 508.5522 | 594905.629 | 39105.2248 | 0.21756
2021-09-21 | 2021-09-21 00:00:00+00:00 | 1.003 | 1.0021 | 1.0054 | 0.97033 | 0.99365 | 1.0031 | 554905.1498 | 51325.7557 | 1278.602 | 15876.9961 | 93820.6173 | 414230.0426 | 65058.3464 | 5517.0234 | 484.1712 | 29508.0317 | 30358.9569 | 510.7357 | 30192.3954 | 30652.7057 | 472.4392 | 30183.2155 | 30323.5377 | 497.4535 | 494.7939 | 471.4402 | 545350.364 | 33823.2844 | 471.0283 | 551642.567 | 512.6629 | 588523.543 | 37548.4751 | 500.6304 | 573856.846 | 36863.963 | 0.22649
2021-09-28 | 2021-09-28 00:00:00+00:00 | 1.0049 | 0.99935 | 1.0032 | 0.97375 | 0.99283 | 1.0015 | 584470.9965 | 50859.6281 | 1282.9875 | 16749.0067 | 91650.6393 | 415624.3362 | 63830.2843 | 5815.2078 | 511.1475 | 31414.6641 | 31964.2519 | 540.3134 | 31999.5966 | 32390.1801 | 500.2725 | 31998.205 | 32119.8811 | 525.7305 | 524.069 | 500.5997 | 576815.515 | 32569.1564 | 497.8527 | 581279.545 | 539.9019 | 617830.956 | 35633.5891 | 529.5268 | 605122.845 | 35127.0945 | 0.22051
2021-10-05 | 2021-10-05 00:00:00+00:00 | 1.0094 | 1.0228 | 1.0263 | 0.98167 | 1.0009 | 1.008 | 424315.6415 | 38663.7185 | 988.481 | 11346.6697 | 68476.896 | 308965.0288 | 69334.7744 | 4235.0468 | 381.7224 | 22191.4907 | 22829.3144 | 401.9092 | 22617.5381 | 23107.3002 | 370.4285 | 22799.2675 | 22911.953 | 391.8158 | 381.7747 | 362.1799 | 410449.312 | 25616.2347 | 366.9646 | 421485.647 | 399.1303 | 449249.881 | 28178.347 | 391.4786 | 440142.199 | 27870.79 | 0.22163
2021-10-12 | 2021-10-12 00:00:00+00:00 | 1.0068 | 1.0076 | 1.0122 | 0.97842 | 0.99768 | 1.0032 | 496324.0935 | 44601.6315 | 1548.2415 | 12822.2839 | 80796.6057 | 357921.3813 | 59690.5634 | 4950.2656 | 451.5648 | 24593.1039 | 25148.1962 | 475.3887 | 25003.5215 | 25428.1141 | 438.8498 | 24864.7706 | 24980.7055 | 463.4767 | 457.8739 | 435.5516 | 486875.251 | 29015.7883 | 435.8686 | 493390.957 | 473.7009 | 525234.711 | 32074.2199 | 464.5542 | 514690.473 | 31604.3221 | 0.22574
2021-10-19 | 2021-10-19 00:00:00+00:00 | 1.0136 | 1.0148 | 1.0182 | 0.98474 | 0.99775 | 0.99974 | 448802.3369 | 39069.0049 | 1649.424 | 8784.5358 | 72029.4542 | 309679.9542 | 46158.4687 | 4495.0144 | 422.0817 | 18805.7945 | 19414.7485 | 443.9532 | 19169.8626 | 19698.2186 | 410.9986 | 19337.1971 | 19569.8749 | 433.0175 | 425.2824 | 404.9959 | 440604.31 | 25394.0378 | 405.4881 | 446397.835 | 439.7285 | 474211.774 | 28093.8383 | 433.9948 | 467560.187 | 27723.814 | 0.23259
2021-10-26 | 2021-10-26 00:00:00+00:00 | 1.0074 | 1.0085 | 1.0181 | 0.98627 | 0.9995 | 1.0026 | 252185.3462 | 23286.7274 | 593.0652 | 5582.1407 | 41398.2273 | 177922.2158 | 30866.0193 | 2533.5595 | 234.788 | 11935.1526 | 12295.9296 | 247.2206 | 12227.2168 | 12466.8213 | 226.5313 | 12315.1525 | 12426.0411 | 241.0043 | 236.7171 | 224.616 | 247337.987 | 15112.0071 | 224.8582 | 250798.84 | 244.3589 | 267290.627 | 16656.42 | 241.1238 | 263457.187 | 16326.4561 | 0.23268
2021-11-02 | 2021-11-02 00:00:00+00:00 | 1.0044 | 1.0046 | 1.0121 | 0.98182 | 0.99647 | 0.99792 | 294296.5317 | 26211.5772 | 1301.278 | 6407.9407 | 48326.8275 | 202763.8282 | 26369.1988 | 2947.4563 | 280.0098 | 12822.7693 | 13071.2973 | 292.1554 | 13035.5384 | 13220.5551 | 269.406 | 12945.063 | 13038.9073 | 286.0826 | 282.6625 | 268.1691 | 289269.392 | 16982.9607 | 268.231 | 292821.275 | 291.3788 | 311451.867 | 18898.1364 | 287.0954 | 306653.348 | 18647.1479 | 0.23834
2021-11-09 | 2021-11-09 00:00:00+00:00 | 1.0047 | 0.99863 | 1.0093 | 0.98604 | 1.0001 | 1.0031 | 351322.2013 | 32541.675 | 941.202 | 9104.0856 | 57910.2916 | 246293.1928 | 36227.4305 | 3529.6596 | 330.253 | 17645.6227 | 18102.5973 | 344.9483 | 17921.6119 | 18251.0291 | 316.1963 | 17899.0974 | 18054.449 | 337.6007 | 334.5048 | 316.6316 | 347575.883 | 20849.916 | 314.7135 | 349396.327 | 342.3819 | 372454.113 | 23321.5864 | 337.5516 | 366994.184 | 22950.9337 | 0.23513
2021-11-16 | 2021-11-16 00:00:00+00:00 | 1.017 | 0.99346 | 1.0016 | 0.99524 | 1.0041 | 1.0024 | 257996.0903 | 25186.957 | 1307.4145 | 4911.6219 | 45396.73 | 181812.8414 | 41902.6207 | 2613.2765 | 254.1653 | 10362.8812 | 10699.624 | 266.4302 | 10583.1075 | 10851.0486 | 243.4033 | 10587.0107 | 10737.9167 | 260.2978 | 259.8878 | 245.0059 | 258764.81 | 16851.8955 | 239.3324 | 256359.365 | 261.5431 | 274277.298 | 17751.5923 | 259.2394 | 271567.377 | 17550.2159 | 0.24969
2021-11-23 | 2021-11-23 00:00:00+00:00 | 1.0119 | 1.0044 | 1.0125 | 0.99066 | 1.0008 | 1.0006 | 281327.0849 | 27441.9985 | 1017.68 | 6195.4371 | 46879.2838 | 192527.0221 | 43935.6627 | 2847.8147 | 273.0498 | 12995.4296 | 13270.0351 | 286.4043 | 13173.0424 | 13351.6066 | 261.4812 | 13068.517 | 13165.3673 | 279.7271 | 276.2771 | 260.3364 | 277966.936 | 17506.254 | 258.409 | 279486.487 | 282.3638 | 299045.983 | 19179.7426 | 279.495 | 295885.678 | 18952.8008 | 0.24349
2021-11-30 | 2021-11-30 00:00:00+00:00 | 1.0019 | 1.0035 | 1.0136 | 0.9859 | 0.99112 | 0.99122 | 255470.9348 | 26900.186 | 952.384 | 6656.1212 | 50257.0079 | 180292.8384 | 34395.6324 | 2611.5343 | 248.2128 | 12509.2836 | 12892.0946 | 257.8363 | 12695.2209 | 12967.7337 | 234.3141 | 12594.2935 | 12695.6937 | 253.0245 | 249.6372 | 233.5079 | 249895.472 | 17928.4943 | 233.8609 | 253592.078 | 256.6421 | 272651.18 | 20052.7359 | 255.2916 | 271021.623 | 19875.9749 | 0.27875
2021-12-07 | 2021-12-07 00:00:00+00:00 | 1.0191 | 1.0141 | 1.0217 | 0.99983 | 0.9988 | 0.99951 | 251974.4696 | 24659.4305 | 870.078 | 6651.9333 | 42738.0762 | 175784.9734 | 29719.013 | 2581.4568 | 244.9761 | 13049.8438 | 13223.9706 | 258.5281 | 12866.914 | 13066.8829 | 234.7681 | 12785.6545 | 12888.501 | 251.7521 | 246.4105 | 231.5084 | 248227.374 | 15854.3564 | 230.3604 | 250097.845 | 251.7937 | 267609.651 | 17442.3381 | 252.0558 | 267911.168 | 17427.8228 | 0.24313
2021-12-14 | 2021-12-14 00:00:00+00:00 | 1.0161 | 0.99676 | 1.0224 | 1.0112 | 1.012 | 1.009 | 176668.4054 | 20277.3584 | 583.402 | 2961.7906 | 35710.4399 | 125002.4544 | 28015.2478 | 1827.5993 | 178.1811 | 7316.7463 | 7450.8531 | 188.5329 | 7279.7528 | 7442.045 | 166.8973 | 7225.8678 | 7274.9764 | 183.357 | 179.3391 | 167.4403 | 176038.582 | 13308.9071 | 164.2575 | 174931.667 | 181.3217 | 189238.325 | 14859.1555 | 181.1793 | 189150.175 | 14774.3973 | 0.28568
2021-12-21 | 2021-12-21 00:00:00+00:00 | 1.0216 | 1.0133 | 1.0184 | 0.99964 | 0.99805 | 0.99509 | 272159.0873 | 25471.8432 | 1267.362 | 4295.7178 | 45945.9815 | 185090.8048 | 28114.3304 | 2781.8998 | 270.9554 | 10886.4936 | 11163.5003 | 286.9161 | 10756.2574 | 11021.575 | 261.6138 | 10705.1289 | 10911.8025 | 278.9358 | 273.8931 | 258.1701 | 268932.855 | 16558.8676 | 256.0733 | 269765.198 | 279.0373 | 287831.896 | 18345.8427 | 279.4817 | 288314.529 | 18390.625 | 0.24823
2021-12-28 | 2021-12-28 00:00:00+00:00 | 1.0233 | 1.0237 | 1.0266 | 1.0034 | 1.0037 | 1.002 | 213355.0793 | 21273.8556 | 843.684 | 4472.5636 | 38107.7276 | 151529.4518 | 41230.9558 | 2184.4118 | 211.2231 | 9531.6935 | 9741.7318 | 223.1485 | 9425.7453 | 9640.6803 | 202.5573 | 9358.773 | 9509.8908 | 217.1858 | 211.5544 | 197.8594 | 208208.372 | 14668.1514 | 197.943 | 211142.141 | 216.4416 | 226187.028 | 15746.0682 | 216.3849 | 226027.08 | 15664.3394 | 0.25149
2022-01-04 | 2022-01-04 00:00:00+00:00 | 0.98413 | 0.97101 | 0.97216 | 0.94312 | 0.95472 | 0.94992 | 198946.0417 | 33005.6544 | 1072.042 | 1626.7661 | 56074.8996 | 140958.0234 | 33372.9859 | 2102.2331 | 194.1525 | 6733.9053 | 6871.1211 | 209.7973 | 6727.8132 | 6854.9878 | 185.59 | 6526.284 | 6617.9929 | 201.9749 | 207.7579 | 191.1299 | 196732.962 | 20231.8985 | 188.5835 | 196929.369 | 214.1561 | 220011.65 | 24501.7603 | 211.555 | 217305.072 | 24092.6239 | 0.39781
2022-01-11 | 2022-01-11 00:00:00+00:00 | 0.95792 | 0.93325 | 1.0146 | 0.99243 | 1.0087 | 1.0057 | 244854.8663 | 54954.2363 | 754.65 | 2273.0566 | 103823.1231 | 175312.819 | 40974.3339 | 2665.4005 | 258.5188 | 9222.4187 | 9415.2984 | 274.493 | 9165.7193 | 9314.2936 | 219.0599 | 9102.9207 | 9220.2139 | 266.5059 | 262.6772 | 234.7275 | 244609.006 | 36514.1461 | 228.6835 | 242215.899 | 268.5392 | 280444.844 | 45703.8477 | 264.2056 | 275203.637 | 43530.8507 | 0.59222
2022-01-18 | 2022-01-18 00:00:00+00:00 | 1.0056 | 0.99775 | 1.0152 | 0.99437 | 0.99868 | 0.99756 | 190072.6497 | 25873.2999 | 781.905 | 4028.621 | 46394.0389 | 134784.1496 | 41882.0375 | 1984.5206 | 190.2515 | 8319.6509 | 8472.2313 | 197.8444 | 8374.4438 | 8531.6071 | 176.0412 | 8356.7985 | 8435.8654 | 194.048 | 191.1424 | 176.439 | 187226.983 | 17557.7006 | 175.0563 | 188523.753 | 195.1462 | 206648.849 | 19853.7493 | 194.3037 | 205620.087 | 19433.0561 | 0.34421
2022-01-25 | 2022-01-25 00:00:00+00:00 | 0.99631 | 0.97407 | 0.97853 | 0.96788 | 0.99464 | 0.99208 | 213368.101 | 23774.7459 | 461.1915 | 1646.7812 | 43080.7248 | 150712.5552 | 21996.4964 | 2143.6188 | 206.7589 | 7696.1651 | 7881.7444 | 220.1271 | 7667.5464 | 7853.5985 | 199.861 | 7578.7096 | 7661.6924 | 213.443 | 218.1261 | 205.1814 | 214718.078 | 15310.2307 | 200.6022 | 212182.167 | 220.5256 | 228952.862 | 17469.4816 | 214.5939 | 222760.034 | 17114.9942 | 0.28585
2022-02-01 | 2022-02-01 00:00:00+00:00 | 1.0043 | 0.9789 | 0.99395 | 0.98688 | 1.005 | 1.005 | 310755.9463 | 55337.5591 | 781.804 | 4463.5785 | 122761.7371 | 213516.0342 | 28843.9923 | 3279.9263 | 311.9433 | 12861.1169 | 13127.1585 | 328.8119 | 12776.2558 | 12971.0984 | 286.321 | 12652.9311 | 12741.4136 | 320.3776 | 322.3279 | 292.4917 | 312634.624 | 40805.5485 | 285.0984 | 308508.811 | 324.6379 | 346796.886 | 51481.6155 | 318.7777 | 339802.491 | 49014.6183 | 0.57495
2022-02-08 | 2022-02-08 00:00:00+00:00 | 1.0277 | 0.99453 | 1.0045 | 0.98753 | 1.0145 | 1.013 | 309442.3958 | 73004.815 | 740.788 | 1733.145 | 145576.5294 | 218524.7236 | 35726.6844 | 3348.9715 | 326.6971 | 11338.9797 | 11504.6815 | 341.4539 | 11100.0026 | 11376.095 | 295.2768 | 10885.6061 | 10990.7573 | 334.0755 | 332.5658 | 296.9017 | 312671.685 | 49813.798 | 287.3266 | 306934.093 | 338.2954 | 357237.357 | 64419.3579 | 329.3055 | 346475.93 | 60096.3604 | 0.66618
2022-02-15 | 2022-02-15 00:00:00+00:00 | 1.0219 | 1.0011 | 1.0138 | 0.99438 | 1.0088 | 1.0077 | 369200.0258 | 56443.8946 | 1770.0175 | 5144.994 | 105214.787 | 268590.9578 | 68745.8029 | 3855.3715 | 374.5297 | 13849.691 | 14383.2443 | 391.9935 | 13797.0233 | 14269.6587 | 348.8974 | 13761.1692 | 14016.4976 | 383.2616 | 378.0631 | 348.4984 | 368147.568 | 38549.8215 | 341.4163 | 366374.252 | 385.4263 | 406107.797 | 44335.798 | 379.9008 | 399832.4774 | 42729.7339 | 0.39173
2022-02-22 | 2022-02-22 00:00:00+00:00 | 1.0027 | 0.98965 | 1.0151 | 0.99078 | 1.0069 | 1.0073 | 362233.4021 | 59179.225 | 800.1063 | 4057.7261 | 119510.2753 | 261127.0946 | 50868.7855 | 3796.0883 | 360.7755 | 14230.5622 | 14677.4617 | 379.687 | 14187.175 | 14531.89 | 331.6631 | 14217.1737 | 14305.0889 | 370.2313 | 364.7076 | 335.1318 | 359427.238 | 41471.1689 | 330.7724 | 359469.325 | 373.6764 | 400363.544 | 51961.7495 | 367.7038 | 393211.503 | 49322.261 | 0.45767
2022-03-01 | 2022-03-01 00:00:00+00:00 | 1.0142 | 0.9815 | 0.98479 | 0.98189 | 1.0049 | 1.0058 | 358780.2943 | 61552.9056 | 697.88 | 2503.6353 | 142232.2012 | 256610.7882 | 35462.7906 | 3748.9097 | 353.0653 | 13113.5588 | 13476.6948 | 375.8236 | 13098.2512 | 13356.2314 | 331.9769 | 12964.5313 | 13065.0669 | 364.4444 | 370.074 | 338.2331 | 363622.318 | 47511.8068 | 327.341 | 356229.678 | 371.1646 | 398771.629 | 58182.1141 | 362.676 | 388520.202 | 54698.8851 | 0.55427
2022-03-08 | 2022-03-08 00:00:00+00:00 | 0.98499 | 0.98049 | 1.01 | 0.98471 | 0.99865 | 1.0037 | 310549.568 | 34543.8738 | 632.3445 | 6361.2748 | 62427.0638 | 233733.4681 | 56948.1101 | 3153.9688 | 288.2729 | 9713.3776 | 15545.0831 | 303.8949 | 14844.4534 | 15365.0457 | 269.9051 | 15097.8 | 15192.3135 | 296.0839 | 293.1486 | 275.2747 | 306049.278 | 24528.1903 | 274.0193 | 308552.478 | 300.6801 | 332557.756 | 28901.7091 | 296.4841 | 327405.273 | 27809.4595 | 0.26709
2022-03-15 | 2022-03-15 00:00:00+00:00 | 0.99767 | 0.96776 | 0.99543 | 0.98471 | 0.99925 | 0.99941 | 436492.185 | 57273.4999 | 1330.86 | 2866.5929 | 118208.9481 | 321942.4682 | 56373.861 | 4492.3496 | 427.074 | 0 | 15053.86 | 451.2561 | 14345.1683 | 14943.2469 | 399.797 | 14579.0172 | 14830.7227 | 439.1651 | 441.1833 | 413.1158 | 441594.831 | 40808.6789 | 400.729 | 433526.031 | 445.9861 | 473904.904 | 47247.5137 | 439.4946 | 466371.396 | 45625.8493 | 0.36717
2022-03-22 | 2022-03-22 00:00:00+00:00 | 1.0194 | 0.99328 | 1.0017 | 0.98762 | 1.0025 | 1.0057 | 355675.1711 | 53275.4921 | 780.24 | 5062.1963 | 101820.7047 | 280365.1552 | 92225.9941 | 3701.7807 | 341.1224 | 0 | 15582.8244 | 359.197 | 15037.971 | 15532.5085 | 321.4174 | 15213.7741 | 15261.6501 | 350.1597 | 349.5779 | 323.5904 | 356635.262 | 38173.2973 | 315.31 | 352514.442 | 354.55 | 390116.406 | 42666.6054 | 349.2817 | 383554.091 | 41270.8214 | 0.36317
2022-03-29 | 2022-03-29 00:00:00+00:00 | 1.0137 | 0.99352 | 1.0009 | 0.99332 | 1.0008 | 1.004 | 499586.5027 | 35137.1521 | 1809.412 | 9331.9742 | 67928.1237 | 393358.5625 | 119298.8322 | 4979.2907 | 462.409 | 0 | 21302.4081 | 485.481 | 20455.236 | 21118.4535 | 450.5063 | 20826.7957 | 20997.4083 | 473.945 | 473.5402 | 453.4466 | 499855.474 | 27263.0008 | 444.4322 | 496009.364 | 477.131 | 521291.775 | 27492.1613 | 473.557 | 517272.575 | 27427.0991 | 0.17269
2022-04-05 | 2022-04-05 00:00:00+00:00 | 1.0064 | 0.99715 | 1.0052 | 0.98577 | 0.99757 | 1.0014 | 462958.1024 | 31847.2277 | 1190.446 | 5903.5957 | 65220.6371 | 364742.7246 | 82003.6341 | 4587.1941 | 425.5554 | 0 | 18715.1341 | 446.0098 | 17964.4716 | 18583.1284 | 415.2058 | 18324.9037 | 18334.5617 | 435.7826 | 433.5346 | 416.3906 | 459628.058 | 25115.0211 | 412.5523 | 460145.01 | 442.0731 | 482939.805 | 26109.1865 | 436.8425 | 476914.904 | 25921.7658 | 0.17881
2022-04-12 | 2022-04-12 00:00:00+00:00 | 1.0124 | 0.97 | 0.97683 | 0.98898 | 0.9966 | 0.99887 | 320699.4247 | 23703.4799 | 1459.886 | 5386.7585 | 45903.1824 | 247388.589 | 83654.7844 | 3200.834 | 297.7183 | 0 | 13085.5813 | 315.5914 | 12697.3611 | 13052.4658 | 291.5341 | 12743.2361 | 12898.9214 | 306.6548 | 313.9301 | 300.5511 | 327165.7393 | 18217.8296 | 287.9579 | 317912.371 | 310.0711 | 335025.226 | 18348.4788 | 307.7015 | 332081.882 | 18244.5005 | 0.18555
2022-04-19 | 2022-04-19 00:00:00+00:00 | 1.0093 | 0.97656 | 0.98577 | 0.98418 | 0.99207 | 0.99428 | 658271.2554 | 47956.9287 | 2616.751 | 7668.1424 | 96951.2499 | 504806.2792 | 117190.2016 | 6568.8485 | 613.343 | 0 | 24003.5486 | 646.5154 | 23349.7957 | 24131.3872 | 600.2159 | 23677.4567 | 24048.8333 | 629.9292 | 639.024 | 614.6225 | 667830.855 | 36354.0611 | 594.7133 | 653723.167 | 640.0517 | 688322.124 | 37581.5127 | 634.9632 | 682641.874 | 37473.9288 | 0.19206
2022-04-26 | 2022-04-26 00:00:00+00:00 | 0.97312 | 0.96107 | 1.0011 | 0.98087 | 0.99625 | 1.0026 | 678301.3128 | 50177.2775 | 1805.725 | 12253.2687 | 101254.8678 | 523639.1254 | 119599.6033 | 6719.5248 | 607.3661 | 0 | 30060.8052 | 637.2944 | 29277.607 | 29958.0771 | 573.7521 | 14688.2408 | 29559.2316 | 622.3303 | 621.6631 | 596.9953 | 673510.006 | 38641.7372 | 589.6009 | 673954.036 | 634.468 | 710108.608 | 40583.1228 | 624.6746 | 698588.175 | 40228.9841 | 0.19337
2022-05-03 | 2022-05-03 00:00:00+00:00 | 0.99003 | 0.94468 | 0.97637 | 0.98833 | 0.99779 | 1.003 | 543415.9816 | 42910.788 | 1876.05 | 9656.2924 | 84975.0729 | 435965.1246 | 117656.8674 | 5434.7922 | 495.1871 | 0 | 23914.8473 | 520.2281 | 23288.7426 | 23778.7056 | 470.7034 | 0 | 23506.0095 | 507.7076 | 519.9971 | 498.2692 | 556999.25 | 32971.7405 | 475.4417 | 539107.506 | 513.7001 | 570223.15 | 33284.0411 | 508.8343 | 564386.852 | 33248.8717 | 0.19491
2022-05-10 | 2022-05-10 00:00:00+00:00 | 1.0092 | 0.99675 | 1.0083 | 0.99058 | 1.0019 | 1.0086 | 552730.5951 | 42879.5392 | 1577.3455 | 12269.8077 | 80747.5897 | 442151.9456 | 168476.8952 | 5512.5786 | 495.1324 | 0 | 26833.8307 | 520.9 | 26002.7783 | 26654.4396 | 479.6484 | 23141.8102 | 26584.598 | 508.0162 | 503.8355 | 481.2145 | 547024.537 | 33157.8862 | 475.2691 | 547713.775 | 512.8474 | 578802.657 | 33840.3611 | 507.0701 | 571803.064 | 33672.9199 | 0.18262
2022-05-17 | 2022-05-17 00:00:00+00:00 | 1.0093 | 0.98019 | 0.98689 | 0.97895 | 0.99692 | 1.0055 | 788457.5807 | 59552.0064 | 1994.216 | 17084.8845 | 115264.5288 | 616744.435 | 116673.6006 | 7799.0442 | 690.9539 | 0 | 37532.2851 | 728.3385 | 36925.5891 | 37497.2961 | 679.5557 | 36993.853 | 37438.6886 | 709.6462 | 719.0717 | 693.2889 | 798481.85 | 43336.0263 | 673.316 | 783726.677 | 724.904 | 826788.364 | 44829.9761 | 711.8368 | 811225.994 | 44376.4633 | 0.18689
2022-05-24 | 2022-05-24 00:00:00+00:00 | 1.0238 | 1.0008 | 1.0059 | 0.99195 | 1.0035 | 1.0111 | 464831.2552 | 54843.4315 | 1194.8385 | 9921.0563 | 99925.0923 | 401358.3506 | 148134.1579 | 4756.7883 | 421.4831 | 0 | 23170.4819 | 445.1096 | 22779.3155 | 23105.3012 | 405.1625 | 22809.4293 | 22997.4407 | 433.2963 | 430.7593 | 404.8279 | 464190.838 | 40912.1821 | 395.7279 | 460339.914 | 436.8131 | 499235.78 | 45317.823 | 431.7889 | 492747.024 | 44406.2052 | 0.24897
2022-05-31 | 2022-05-31 00:00:00+00:00 | 1.0218 | 0.99835 | 1.0102 | 0.99812 | 1.0077 | 1.0154 | 573108.6255 | 45342.4008 | 1500.556 | 12942.3113 | 84738.9498 | 464961.12 | 122958.7511 | 5731.2805 | 512.6919 | 0 | 27822.6313 | 539.7991 | 27214.432 | 27712.5269 | 499.2772 | 27526.9375 | 27674.5972 | 526.2455 | 520.9513 | 500.1038 | 575213.456 | 32957.0192 | 488.6247 | 568508.761 | 527.2384 | 601080.134 | 34899.036 | 522.2253 | 594851.99 | 34751.267 | 0.18225

## IEC_7d_5sigma
|  | ppi_2Mono | ppi_1BMono | ppi_1B | ppi_2A | ppi_2B | Gfront_poa | Grear | row2wind_speed | temp_ambient_FieldAverage | albedo_down | albedo_up | SRRL_DHI | Hydra_avg | power_dc_inv2 | row2tmod_1 | row2tmod_2 | power_dc_inv4 | row4tmod_1 | row4tmod_2 | power_dc_inv8 | row8tmod_1 | row8tmod_2 | power_dc_inv2+4 | power_dc_inv2+4_1B | power_dc_inv8_1B | Gfront_poa_1B | Grear_1B | power_dc_inv8_2Mono | Gfront_poa_2Mono | power_dc_inv8_2A | Gfront_poa_2A | Grear_2A | power_dc_inv8_2B | Gfront_poa_2B | Grear_2B | albedo_actual
2021-06-08 | 2021-06-08 00:00:00+00:00 | 1.0153 | 1.0019 | 1.0111 | 0.98862 | 1.0189 | 656182.7297 | 47956.5689 | 1093.8137 | 17115.2991 | 91800.9456 | 505823.4778 | 87425.6426 | 6470.7939 | 564.2804 | 34055.1983 | 34652.3436 | 586.9611 | 34005.4498 | 34932.1629 | 550.4202 | 34943.2044 | 35091.4633 | 575.6208 | 569.2811 | 549.3616 | 653340.203 | 33784.6854 | 542.1118 | 652185.258 | 582.2466 | 686775.327 | 36290.9257 | 564.9536 | 664696.392 | 35787.4445 | 0.18149
2021-06-15 | 2021-06-15 00:00:00+00:00 | 1.0137 | 0.99439 | 0.99953 | 0.98225 | 1.0165 | 802076.3929 | 64264.2203 | 1392.1455 | 21959.9744 | 128905.0673 | 633685.1584 | 93111.3565 | 7923.6125 | 681.7061 | 43155.3839 | 43550.4661 | 712.8147 | 43010.2244 | 43781.3787 | 666.9621 | 43552.4366 | 43749.4325 | 697.2604 | 697.5875 | 670.7224 | 804689.76 | 47025.3051 | 657.9184 | 797438.798 | 709.8632 | 844017.264 | 49853.2418 | 685.9361 | 813354.048 | 48987.9108 | 0.20342
2021-06-22 | 2021-06-22 00:00:00+00:00 | 1.0241 | 0.99564 | 0.99906 | 0.99272 | 1.0282 | 492546.9121 | 46173.9903 | 1004.362 | 17039.9254 | 87165.9502 | 404214.363 | 125398.5524 | 4910.9519 | 423.3566 | 29578.8001 | 29894.624 | 442.2921 | 29753.005 | 30227.75 | 409.4685 | 30116.2458 | 30304.3518 | 432.8243 | 433.2312 | 411.2607 | 494581.303 | 34473.2468 | 399.8181 | 488059.626 | 436.0003 | 521681.65 | 36033.3362 | 420.9387 | 502612.11 | 35482.5612 | 0.21564
2021-06-29 | 2021-06-29 00:00:00+00:00 | 1.0197 | 0.99098 | 1.0068 | 0.99697 | 1.0237 | 335208.0043 | 33180.3247 | 624.9455 | 9121.1946 | 56745.0718 | 283745.9242 | 117091.7282 | 3366.9182 | 298.6389 | 17835.0099 | 18096.191 | 310.7382 | 17946.309 | 18395.7934 | 285.3994 | 18257.2733 | 18414.3455 | 304.6885 | 302.6434 | 287.9981 | 337536.248 | 23493.7753 | 279.8881 | 331765.471 | 305.6142 | 355561.367 | 23773.2811 | 297.6252 | 345267.637 | 23294.8779 | 0.19999
2021-07-06 | 2021-07-06 00:00:00+00:00 | 1.0106 | 1 | 1.0107 | 0.98339 | 1.0164 | 502681.1116 | 41922.7027 | 821.1235 | 13456.2225 | 74377.751 | 387446.3542 | 87326.0933 | 4977.1458 | 432.8187 | 26913.1447 | 27304.3007 | 451.5577 | 27016.1583 | 27634.3445 | 420.4074 | 27517.6433 | 27641.8606 | 442.1882 | 437.5031 | 420.4034 | 498038.113 | 27975.891 | 415.9985 | 499151.691 | 449.6585 | 529412.349 | 30124.4489 | 435.0611 | 510838.215 | 29680.282 | 0.19197
2021-07-13 | 2021-07-13 00:00:00+00:00 | 1.0238 | 1.0013 | 1.0085 | 0.99348 | 1.0269 | 570194.5788 | 50868.9209 | 1051.092 | 17782.1111 | 91162.5229 | 461725.953 | 113105.9297 | 5676.1682 | 490.8268 | 33280.4896 | 33352.9622 | 513.0746 | 33300.5244 | 33707.4295 | 475.8921 | 33593.2401 | 33772.9598 | 501.9507 | 497.7446 | 475.2978 | 570081.927 | 35333.048 | 464.8501 | 565600.168 | 505.2453 | 602788.952 | 37979.6551 | 488.7894 | 581856.006 | 37494.6725 | 0.19744
2021-07-20 | 2021-07-20 00:00:00+00:00 | 1.0183 | 0.99625 | 1.0046 | 0.98878 | 1.0232 | 523877.2306 | 45355.6822 | 981.63 | 16214.578 | 80754.6309 | 414485.3906 | 103376.9547 | 5201.0491 | 449.1177 | 30231.3778 | 30288.942 | 469.6134 | 30319.304 | 30724.5357 | 435.8873 | 30633.0196 | 30884.071 | 459.3656 | 457.2543 | 437.5292 | 523687.601 | 31039.4455 | 428.0337 | 519852.502 | 464.5775 | 553027.745 | 33190.3928 | 448.9646 | 533380.564 | 32903.2167 | 0.19483
2021-07-27 | 2021-07-27 00:00:00+00:00 | 1.0136 | 0.99921 | 1.0073 | 0.98337 | 1.0187 | 520441.7426 | 46321.2812 | 986.984 | 17043.1817 | 81020.8926 | 427826.3002 | 109635.0058 | 5173.8271 | 441.3492 | 30910.8088 | 30913.2641 | 462.2098 | 30996.2922 | 31410.2308 | 428.3012 | 31255.0294 | 31545.0612 | 451.7795 | 448.4989 | 428.6415 | 517533.259 | 31641.5399 | 422.5586 | 516497.628 | 459.4207 | 550345.974 | 33223.5846 | 443.4912 | 530079.005 | 32754.985 | 0.18938
2021-08-03 | 2021-08-03 00:00:00+00:00 | 1.0172 | 1.0054 | 1.0131 | 0.98701 | 1.0205 | 521397.8047 | 47301.6615 | 984.298 | 16479.4189 | 80007.8774 | 435270.6362 | 122767.3077 | 5195.6975 | 446.6798 | 30804.1466 | 30967.7598 | 468.5488 | 30653.5018 | 31289.1978 | 433.1728 | 31018.8618 | 31380.574 | 457.6143 | 451.6806 | 430.8642 | 516472.363 | 32066.3724 | 425.8418 | 517251.722 | 463.6348 | 551801.111 | 33561.2521 | 448.4158 | 532550.171 | 33107.3784 | 0.18381
2021-08-10 | 2021-08-10 00:00:00+00:00 | 1.0294 | 1.0028 | 1.0081 | 0.9983 | 1.03 | 495843.5249 | 46163.5953 | 1223.752 | 17042.5822 | 73725.7757 | 409070.1656 | 160492.6683 | 4953.8522 | 433.7894 | 28902.055 | 29709.2101 | 455.1087 | 29527.2078 | 30150.9004 | 419.9993 | 29839.5341 | 30087.8564 | 444.4491 | 440.8655 | 418.8079 | 495185.658 | 31194.4913 | 408.0197 | 490933.714 | 445.2039 | 524649.781 | 32258.4192 | 431.5083 | 507897.709 | 32044.6509 | 0.18023
2021-08-17 | 2021-08-17 00:00:00+00:00 | 1.0185 | 1.0022 | 1.0079 | 0.98679 | 1.0216 | 596008.9742 | 52456.3892 | 1286.6008 | 19512.2433 | 86723.8276 | 476486.659 | 133968.5258 | 5918.2176 | 513.6743 | 34041.1697 | 34984.9516 | 539.8421 | 34675.4251 | 35378.9659 | 499.9766 | 35096.6438 | 35421.2519 | 526.7582 | 522.6405 | 498.869 | 591651.954 | 34829.7783 | 490.9146 | 591397.1 | 533.8093 | 629879.091 | 36638.9129 | 515.6123 | 607485.63 | 36326.3379 | 0.18201
2021-08-24 | 2021-08-24 00:00:00+00:00 | 1.006 | 0.99976 | 1.0058 | 0.9732 | 1.011 | 513688.8553 | 43035.7571 | 1182.714 | 14556.7416 | 71943.4195 | 397378.0838 | 84744.1157 | 5060.3269 | 441.2662 | 26594.9975 | 27345.6544 | 464.3699 | 27222.907 | 27764.3279 | 432.2851 | 27408.4872 | 27644.5272 | 452.818 | 450.2253 | 432.3868 | 506860.194 | 27375.1517 | 429.724 | 510421.453 | 465.2854 | 541618.612 | 29111.5662 | 447.8874 | 520387.741 | 28671.5514 | 0.18105
2021-08-31 | 2021-08-31 00:00:00+00:00 | 1.0018 | 0.99631 | 1.0032 | 0.9707 | 1.01 | 569215.6208 | 48314.6971 | 1148.0005 | 17207.4737 | 82750.389 | 424077.1822 | 83349.7633 | 5606.8764 | 484.5081 | 31041.6817 | 32127.8846 | 509.6903 | 31806.1194 | 32541.0604 | 473.5385 | 32171.2263 | 32428.7382 | 497.0992 | 495.5307 | 475.292 | 560837.792 | 30602.708 | 472.6908 | 565674.466 | 512.1034 | 600628.697 | 33052.4544 | 492.1915 | 575969.093 | 32527.3568 | 0.19513
2021-09-07 | 2021-09-07 00:00:00+00:00 | 1.0082 | 0.99607 | 1.0007 | 0.97508 | 1.0105 | 476345.2859 | 43978.203 | 1228.2755 | 15197.4478 | 76571.0387 | 358412.8916 | 92667.7082 | 4733.0496 | 413.0249 | 26290.7489 | 27123.5597 | 434.6668 | 26855.3959 | 27339.9366 | 402.0699 | 26978.8953 | 27119.0875 | 423.8458 | 423.5378 | 403.6569 | 471775.684 | 29035.9449 | 398.8065 | 473032.33 | 434.6762 | 505010.521 | 30410.9981 | 419.4315 | 486510.817 | 29995.3803 | 0.21364
2021-09-14 | 2021-09-14 00:00:00+00:00 | 1.0151 | 0.99993 | 1.0026 | 0.98044 | 1.0141 | 537042.8039 | 51646.1799 | 1154.804 | 18105.8749 | 90368.589 | 414553.9144 | 105360.297 | 5365.1941 | 464.7845 | 31322.7791 | 32402.8138 | 489.8754 | 31928.9777 | 32572.1326 | 451.9495 | 32135.576 | 32371.0653 | 477.3299 | 476.0685 | 451.9824 | 533170.663 | 34781.5181 | 445.2343 | 533110.312 | 486.8542 | 570585.684 | 36842.7036 | 470.7088 | 550905.791 | 36280.9436 | 0.21799
2021-09-21 | 2021-09-21 00:00:00+00:00 | 1.0043 | 0.99735 | 1.0012 | 0.97119 | 1.0048 | 517040.0682 | 47510.5481 | 1170.204 | 14551.0181 | 87209.8241 | 387319.929 | 54707.3367 | 5134.4772 | 451.5102 | 27208.9433 | 28011.9848 | 475.9639 | 27895.5673 | 28323.9816 | 440.8094 | 27876.9797 | 27991.5814 | 463.7371 | 463.1918 | 441.982 | 511749.017 | 31093.4578 | 438.9246 | 514202.222 | 477.4952 | 548332.917 | 34006.9862 | 461.5128 | 528880.673 | 33169.4666 | 0.22516
2021-09-28 | 2021-09-28 00:00:00+00:00 | 1.0101 | 1.0046 | 1.0088 | 0.9787 | 1.0074 | 570117.3823 | 49843.3792 | 1244.662 | 16214.0677 | 89914.6897 | 407768.5904 | 61307.2889 | 5670.0973 | 501.9364 | 30466.113 | 31018.261 | 529.2332 | 31056.1784 | 31445.8508 | 490.551 | 31048.6731 | 31159.1742 | 515.5848 | 511.1045 | 488.3203 | 562809.81 | 31958.7492 | 485.6619 | 567049.007 | 526.8044 | 602862.361 | 34900.7426 | 511.8157 | 584562.304 | 34179.9825 | 0.2205
2021-10-05 | 2021-10-05 00:00:00+00:00 | 1.0072 | 1.0075 | 1.0133 | 0.9797 | 1.0066 | 382760.0602 | 34294.6847 | 871.839 | 10186.0426 | 61250.7593 | 280302.5562 | 53343.8298 | 3815.1181 | 343.2126 | 19884.6138 | 20446.9346 | 360.9791 | 20280.181 | 20710.088 | 333.226 | 20434.0225 | 20537.3416 | 352.0959 | 347.4806 | 330.7456 | 375401.339 | 22347.9643 | 330.8291 | 380434.795 | 359.39 | 405054.341 | 24260.4951 | 349.7988 | 393630.331 | 23856.6296 | 0.21852
2021-10-12 | 2021-10-12 00:00:00+00:00 | 1.0064 | 1.0051 | 1.0105 | 0.97828 | 1.0032 | 478464.1186 | 42812.2158 | 1483.3255 | 12206.6152 | 77720.1455 | 344562.0253 | 54479.3613 | 4770.4582 | 435.6623 | 23524.0887 | 24060.2135 | 457.9503 | 23935.8342 | 24339.4422 | 423.0545 | 23806.2436 | 23910.8733 | 446.8063 | 442.1491 | 420.899 | 470480.548 | 27739.3449 | 420.3665 | 475735.201 | 456.7283 | 506300.298 | 30520.6692 | 445.3921 | 493104.969 | 29901.4371 | 0.22556
2021-10-19 | 2021-10-19 00:00:00+00:00 | 1.0122 | 1.0088 | 1.013 | 0.98352 | 0.99858 | 425719.9196 | 36698.6874 | 1580.524 | 8341.0409 | 68245.9801 | 294695.3594 | 37339.1528 | 4261.8314 | 399.9035 | 17807.6028 | 18376.4149 | 420.2561 | 18154.7942 | 18652.6499 | 389.4318 | 18307.7801 | 18530.6285 | 410.0798 | 404.8361 | 386.0354 | 420199.518 | 23602.5838 | 384.747 | 423595.72 | 416.9497 | 449693.259 | 26159.577 | 410.6624 | 442300.293 | 25715.0579 | 0.23158
2021-10-26 | 2021-10-26 00:00:00+00:00 | 1.0096 | 1.0049 | 1.0138 | 0.98628 | 1.0031 | 237849.6248 | 21794.3822 | 557.58 | 5323.4886 | 38918.4865 | 168496.5594 | 26616.7184 | 2388.5082 | 221.958 | 11340.7891 | 11679.7715 | 232.9688 | 11604.302 | 11830.9151 | 214.1564 | 11691.4914 | 11797.2097 | 227.4634 | 224.3644 | 213.1073 | 234801.538 | 14052.3927 | 212.1198 | 236594.889 | 230.6265 | 252072.058 | 15405.2967 | 226.7567 | 247420.616 | 15059.5999 | 0.23097
2021-11-02 | 2021-11-02 00:00:00+00:00 | 1.0111 | 1.0108 | 1.018 | 0.98784 | 1.0043 | 285466.8113 | 25354.2971 | 1239.86 | 6172.8304 | 46835.3966 | 196402.5218 | 24285.2307 | 2857.922 | 273.1549 | 12421.4086 | 12659.6474 | 285.2808 | 12624.3522 | 12802.5307 | 263.1275 | 12537.8479 | 12621.7407 | 279.2179 | 274.2942 | 260.3203 | 280823.903 | 16383.7977 | 260.2488 | 284071.085 | 282.654 | 302097.526 | 18218.7736 | 278.0221 | 296938.193 | 17930.5985 | 0.23847
2021-11-09 | 2021-11-09 00:00:00+00:00 | 1.0072 | 1.0101 | 1.0203 | 0.98845 | 1.0057 | 338789.302 | 31227.7612 | 898.554 | 8864.8091 | 55490.4055 | 234529.528 | 33159.3009 | 3402.6903 | 318.92 | 17066.4379 | 17493.6412 | 333.2616 | 17345.9056 | 17648.3675 | 305.5497 | 17316.5087 | 17463.6857 | 326.0908 | 319.6007 | 302.4926 | 332492.042 | 19936.689 | 303.3527 | 337023.181 | 329.9028 | 359154.989 | 22325.9612 | 324.2478 | 352650.663 | 21850.8721 | 0.2366
2021-11-16 | 2021-11-16 00:00:00+00:00 | 1.0168 | 0.99883 | 1.0065 | 0.99536 | 1.0032 | 249190.9631 | 23926.4821 | 1219.9305 | 4679.9736 | 43228.5296 | 173064.763 | 39493.5507 | 2519.917 | 245.2721 | 9957.5539 | 10289.7772 | 256.8789 | 10182.7208 | 10444.8925 | 235.04 | 10191.8832 | 10338.3042 | 251.0755 | 249.462 | 235.3149 | 248562.302 | 15952.0839 | 231.1619 | 247652.201 | 252.2461 | 264644.203 | 16879.4548 | 250.2805 | 262230.781 | 16680.1576 | 0.24978
2021-11-23 | 2021-11-23 00:00:00+00:00 | 1.015 | 1.0015 | 1.0098 | 0.99349 | 1.0034 | 268911.5865 | 26264.4488 | 972.788 | 5975.3035 | 44785.7652 | 184963.3054 | 40791.6288 | 2722.4702 | 261.5016 | 12491.2817 | 12753.0467 | 274.5502 | 12658.9448 | 12828.0765 | 250.5957 | 12550.9565 | 12643.5373 | 268.0259 | 265.4126 | 250.225 | 267329.543 | 16666.659 | 246.8996 | 267192.817 | 269.7826 | 285913.779 | 18073.1884 | 267.1058 | 282896.908 | 17829.2099 | 0.24213
2021-11-30 | 2021-11-30 00:00:00+00:00 | 1.0136 | 1.016 | 1.0223 | 0.99441 | 0.9997 | 246801.5282 | 26000.6844 | 921.248 | 6535.1599 | 47951.1522 | 176531.8038 | 33444.8025 | 2524.1413 | 240.1206 | 12255.5865 | 12626.9625 | 252.5234 | 12402.8209 | 12660.0162 | 228.8295 | 12295.9255 | 12397.2892 | 246.322 | 240.9508 | 225.2368 | 241357.785 | 17492.9882 | 225.7512 | 244992.609 | 247.7065 | 263407.283 | 19530.4693 | 246.397 | 261787.683 | 19327.0839 | 0.27163
2021-12-07 | 2021-12-07 00:00:00+00:00 | 1.019 | 1.0127 | 1.0205 | 0.9997 | 0.99927 | 247929.3693 | 24246.9834 | 859.94 | 6560.3883 | 42001.5661 | 173273.2828 | 29073.8827 | 2540.2944 | 241.0186 | 12839.6571 | 13009.7487 | 254.3544 | 12655.8559 | 12851.4884 | 230.9901 | 12578.1425 | 12679.9209 | 247.6865 | 242.7206 | 228.0925 | 244597.657 | 15566.7682 | 226.6757 | 246096.853 | 247.7599 | 263315.33 | 17065.9498 | 247.867 | 263463.828 | 17032.4395 | 0.2424
2021-12-14 | 2021-12-14 00:00:00+00:00 | 1.0296 | 1.0097 | 1.0219 | 1.012 | 1.0083 | 171146.0012 | 18279.1833 | 569.478 | 2930.9922 | 32189.8646 | 119826.5844 | 26508.6518 | 1764.0555 | 171.8716 | 7121.6383 | 7253.4248 | 181.7693 | 7084.7729 | 7245.3158 | 163.7763 | 7063.6753 | 7185.1072 | 176.8205 | 173.0311 | 162.2054 | 170635.747 | 11880.7032 | 159.0613 | 169514.06 | 174.7202 | 182439.718 | 12896.8045 | 175.3656 | 183121.744 | 12962.1153 | 0.26864
2021-12-21 | 2021-12-21 00:00:00+00:00 | 1.0214 | 1.0112 | 1.0165 | 0.99959 | 0.99505 | 266889.9868 | 24858.2259 | 1212.18 | 4201.5278 | 44840.9652 | 181247.6604 | 27441.9963 | 2727.3121 | 265.6133 | 10672.0444 | 10945.9089 | 281.2594 | 10548.4639 | 10808.9923 | 256.5087 | 10501.1337 | 10703.0697 | 273.4363 | 268.9905 | 253.659 | 264258.458 | 16140.8468 | 251.1349 | 264586.532 | 273.5473 | 282216.371 | 17800.9164 | 274.7958 | 283569.359 | 17887.0484 | 0.2474
2021-12-28 | 2021-12-28 00:00:00+00:00 | 1.0233 | 1.0197 | 1.0229 | 1.0034 | 1.0019 | 209172.9658 | 20742.6687 | 827.172 | 4398.973 | 37128.6136 | 148534.3098 | 39582.902 | 2140.9231 | 206.9935 | 9347.4777 | 9545.2797 | 218.688 | 9246.0738 | 9451.025 | 198.5822 | 9178.6153 | 9326.0636 | 212.8407 | 208.0682 | 194.7459 | 204958.202 | 14242.0624 | 194.068 | 207021.743 | 212.1271 | 221691.794 | 15214.7528 | 212.4414 | 221972.959 | 15162.578 | 0.24997
2022-01-04 | 2022-01-04 00:00:00+00:00 | 1.027 | 1.0071 | 1.0229 | 0.99726 | 0.99766 | 177991.2519 | 30500.4376 | 900.772 | 1536.0238 | 50470.5038 | 129751.6932 | 31156.4872 | 1900.1591 | 184.4502 | 6240.8181 | 6356.3935 | 197.9877 | 6200.1624 | 6317.337 | 172.8342 | 6050.8818 | 6117.1417 | 191.219 | 186.9409 | 171.6124 | 177042.51 | 18729.5 | 168.2908 | 176167.636 | 191.7448 | 197452.681 | 22780.8264 | 191.6684 | 197251.751 | 22362.7791 | 0.38898
2022-01-11 | 2022-01-11 00:00:00+00:00 | 1.027 | 1.0054 | 1.0181 | 0.99771 | 1.0085 | 215568.8046 | 43308.9623 | 679.618 | 2551.978 | 84828.6093 | 151804.802 | 30826.1099 | 2319.4384 | 225.0085 | 8387.5928 | 8543.4601 | 238.4407 | 8329.9179 | 8467.8692 | 206.1278 | 8196.8502 | 8295.8278 | 231.7246 | 227.5986 | 205.0238 | 214572.914 | 29316.1302 | 200.7151 | 213362.335 | 232.2567 | 243510.276 | 36649.0257 | 229.7798 | 240310.346 | 35172.3303 | 0.5588
2022-01-18 | 2022-01-18 00:00:00+00:00 | 1.022 | 1.0143 | 1.0241 | 1.0023 | 1.0053 | 181376.0191 | 24299.8027 | 766.783 | 3952.1214 | 41916.4485 | 128940.1352 | 40489.7626 | 1891.4266 | 182.2844 | 7978.5027 | 8137.425 | 190.6511 | 7997.4876 | 8162.277 | 170.8045 | 8013.3013 | 8085.5652 | 186.4677 | 182.0717 | 168.3946 | 178713.255 | 16140.7939 | 167.1286 | 179916.578 | 186.0417 | 196930.626 | 18261.1934 | 185.4822 | 196210.901 | 17921.2816 | 0.32508
2022-01-25 | 2022-01-25 00:00:00+00:00 | 1.0184 | 1.0067 | 1.0072 | 0.9896 | 0.99975 | 201458.6566 | 21258.9194 | 439.9675 | 1650.6962 | 39266.2792 | 143195.1228 | 20833.727 | 2044.5912 | 199.3004 | 7442.4612 | 7649.3308 | 210.9342 | 7391.1597 | 7587.8916 | 192.821 | 7308.6161 | 7381.8635 | 205.1173 | 203.6464 | 191.5424 | 200630.964 | 14202.8995 | 189.3342 | 200363.012 | 207.272 | 215333.884 | 16326.9361 | 205.1694 | 213008.208 | 15986.774 | 0.27422
2022-02-01 | 2022-02-01 00:00:00+00:00 | 1.027 | 1.0028 | 1.0014 | 0.99462 | 1.0094 | 291478.6371 | 51235.7923 | 755.952 | 4487.6018 | 113966.0267 | 202424.6602 | 25965.133 | 3083.0768 | 294.1523 | 12392.7263 | 12635.4157 | 309.8274 | 12288.8942 | 12452.5075 | 274.3842 | 12126.8335 | 12209.002 | 301.9899 | 301.5728 | 273.6271 | 293075.645 | 38233.8277 | 267.158 | 289419.774 | 303.6244 | 324789.257 | 48628.1765 | 299.1708 | 319286.786 | 46183.5547 | 0.563
2022-02-08 | 2022-02-08 00:00:00+00:00 | 1.0289 | 0.99985 | 1.0086 | 0.98773 | 1.0111 | 286727.5659 | 67406.8025 | 644.648 | 1686.3293 | 133556.5697 | 200679.923 | 28998.6895 | 3107.8816 | 301.6723 | 10644.4513 | 10801.9347 | 316.4648 | 10531.7362 | 10620.2005 | 273.9171 | 10203.261 | 10286.4384 | 309.0685 | 306.4337 | 273.9573 | 288889.281 | 45404.462 | 266.2318 | 284525.917 | 312.9083 | 330812.82 | 59646.6188 | 305.6619 | 321912.993 | 55622.5318 | 0.66552
2022-02-15 | 2022-02-15 00:00:00+00:00 | 1.0249 | 0.99752 | 1.0093 | 0.99592 | 1.0068 | 359003.1826 | 54903.8648 | 1740.6055 | 5096.9718 | 102465.4957 | 262865.7122 | 64861.2391 | 3758.4325 | 364.7057 | 13555.3899 | 14080.1519 | 381.6286 | 13491.6197 | 13952.7587 | 340.2301 | 13458.053 | 13706.0371 | 373.1672 | 369.7415 | 341.0748 | 360477.875 | 37410.5704 | 331.9709 | 356288.175 | 374.6972 | 394911.292 | 43350.5783 | 370.6606 | 390096.328 | 41744.4128 | 0.3898
2022-02-22 | 2022-02-22 00:00:00+00:00 | 1.0194 | 1.0018 | 1.01 | 0.98978 | 1.0062 | 331849.5275 | 51105.4901 | 746.3438 | 3929.863 | 103710.8066 | 237747.4442 | 44419.7046 | 3458.6459 | 328.3013 | 13084.3756 | 13478.8849 | 345.6048 | 13014.3124 | 13335.0533 | 308.6994 | 13083.9921 | 13159.0277 | 336.953 | 333.6184 | 308.1322 | 330960.315 | 35647.1499 | 302.8267 | 329412.979 | 340.4315 | 364823.193 | 43911.8818 | 334.8686 | 358073.592 | 41701.9105 | 0.43622
2022-03-01 | 2022-03-01 00:00:00+00:00 | 1.0173 | 0.98501 | 0.98652 | 0.98383 | 1.0069 | 349899.1288 | 58875.3945 | 679.442 | 2534.6751 | 136664.8187 | 249826.8498 | 34503.5718 | 3652.9633 | 344.8386 | 12836.9783 | 13193.0377 | 365.6406 | 12835.514 | 13092.1934 | 324.5418 | 12718.5992 | 12814.2128 | 355.2396 | 360.0934 | 329.4799 | 354506.434 | 45684.1151 | 319.027 | 347432.267 | 361.0767 | 388128.099 | 55806.8985 | 352.805 | 378127.853 | 52556.6237 | 0.54704
2022-03-08 | 2022-03-08 00:00:00+00:00 | 1.009 | 1.0007 | 1.0056 | 0.98477 | 1.0036 | 285893.6101 | 28232.5619 | 588.744 | 6098.4452 | 50649.6851 | 213335.0938 | 52432.93 | 2881.9987 | 263.4331 | 9514.9651 | 14350.2346 | 277.2613 | 13726.356 | 14193.464 | 254.1232 | 13956.3669 | 14017.4833 | 270.3472 | 268.8439 | 253.9483 | 282750.412 | 20077.1266 | 251.8544 | 284125.902 | 274.5271 | 303845.584 | 22842.3762 | 269.3829 | 297608.87 | 22085.2354 | 0.23742
2022-03-15 | 2022-03-15 00:00:00+00:00 | 1.0155 | 0.98787 | 0.99642 | 0.98526 | 0.99948 | 393827.1298 | 49147.3493 | 1176.832 | 2876.8491 | 101210.7787 | 293448.7386 | 47332.8977 | 4040.3324 | 383.9266 | 0 | 13844.0141 | 404.2294 | 13151.5169 | 13721.0281 | 366.5535 | 13409.8945 | 13570.5272 | 394.078 | 395.4941 | 371.0536 | 397756.05 | 35552.2143 | 360.966 | 391353.726 | 399.974 | 425902.137 | 41136.6299 | 394.2832 | 419252.318 | 39706.6659 | 0.3449
2022-03-22 | 2022-03-22 00:00:00+00:00 | 1.0231 | 0.99366 | 1.0037 | 0.99304 | 1.0101 | 339751.2037 | 47893.1833 | 745.552 | 4883.3035 | 92646.7126 | 266610.9116 | 81642.7809 | 3520.8381 | 325.8728 | 0 | 14855.5563 | 342.866 | 14314.5816 | 14809.4777 | 308.0528 | 14525.3847 | 14572.0005 | 334.3694 | 333.1332 | 310.018 | 341958.524 | 34169.0371 | 301.0845 | 336875.52 | 336.712 | 370619.252 | 37646.1012 | 331.0248 | 363466.293 | 36314.4441 | 0.3475
2022-03-29 | 2022-03-29 00:00:00+00:00 | 1.0175 | 0.99728 | 1.005 | 0.99701 | 1.0082 | 473767.3058 | 33383.1054 | 1695.454 | 8735.7409 | 64867.766 | 375467.1044 | 110486.0775 | 4720.7696 | 440.9851 | 0 | 20030.4759 | 461.0128 | 19264.192 | 19890.1572 | 428.7041 | 19606.0496 | 19759.3485 | 450.9989 | 448.7331 | 429.8713 | 474395.826 | 25893.9552 | 421.3181 | 470453.456 | 452.3512 | 494468.266 | 26031.7172 | 447.3319 | 488677.381 | 25882.4797 | 0.17277
2022-04-05 | 2022-04-05 00:00:00+00:00 | 1.0066 | 0.99239 | 1.001 | 0.98562 | 1.0021 | 441908.7681 | 30345.9262 | 1122.694 | 5645.5068 | 62334.8003 | 349963.1446 | 73704.3939 | 4375.7089 | 406.7083 | 0 | 17807.6825 | 424.8783 | 17110.2287 | 17700.6322 | 396.2777 | 17439.925 | 17444.392 | 415.7933 | 415.3856 | 399.3145 | 441235.236 | 23838.8239 | 393.6955 | 439308.694 | 421.8593 | 461034.875 | 24641.3017 | 414.9097 | 453006.02 | 24373.228 | 0.17812
2022-04-12 | 2022-04-12 00:00:00+00:00 | 1.0163 | 0.9782 | 0.98541 | 0.99238 | 1.0038 | 295629.6509 | 21715.4136 | 1323.68 | 4850.7672 | 42093.4561 | 226733.3196 | 75381.0303 | 2946.0518 | 276.5366 | 0 | 11947.5661 | 290.418 | 11622.0452 | 11961.9987 | 269.7148 | 11654.8161 | 11801.75 | 283.4773 | 287.675 | 275.7268 | 300470.792 | 16578.2365 | 265.3897 | 293198.962 | 285.6536 | 308872.642 | 16667.3579 | 282.4136 | 304926.563 | 16545.6808 | 0.18565
2022-04-19 | 2022-04-19 00:00:00+00:00 | 1.0145 | 0.98252 | 0.99124 | 0.98813 | 0.99977 | 626968.9369 | 45844.935 | 2447.121 | 7208.7166 | 92601.6954 | 482689.7678 | 107752.4942 | 6249.633 | 588.5618 | 0 | 22627.4975 | 615.6026 | 22045.9157 | 22792.9955 | 574.2107 | 22340.0164 | 22686.9745 | 602.0822 | 607.4 | 584.4258 | 635726.752 | 34683.126 | 566.0283 | 622770.236 | 609.3141 | 655837.75 | 35737.037 | 602.22 | 647941.969 | 35584.9176 | 0.19185
2022-04-26 | 2022-04-26 00:00:00+00:00 | 1.0007 | 0.9877 | 1.0004 | 0.98011 | 1.0035 | 612180.5332 | 45037.1113 | 1608.601 | 10762.9796 | 91544.2046 | 474804.9484 | 99923.0637 | 6052.3318 | 548.6888 | 0 | 26620.7215 | 574.6382 | 25977.2612 | 26598.0523 | 533.1389 | 13581.0085 | 26078.0512 | 561.6635 | 561.424 | 539.7785 | 608892.675 | 34544.3507 | 532.7772 | 608502.588 | 573.0618 | 640930.21 | 35996.8859 | 559.7226 | 625034.546 | 35490.0201 | 0.1928
2022-05-03 | 2022-05-03 00:00:00+00:00 | 1.0032 | 0.97705 | 0.99701 | 0.99032 | 1.0086 | 502526.8985 | 38202.8055 | 1471.274 | 8865.8015 | 76136.4403 | 390039.8274 | 104204.6142 | 5000.9739 | 457.5213 | 0 | 22159.6374 | 479.5033 | 21636.2572 | 22074.1871 | 440.277 | 0 | 21789.3304 | 468.5123 | 469.9152 | 450.6202 | 505279.236 | 29413.4469 | 438.8744 | 498863.535 | 473.0921 | 526563.397 | 30146.1352 | 464.5198 | 516432.913 | 29973.9086 | 0.1952
2022-05-10 | 2022-05-10 00:00:00+00:00 | 1.0198 | 0.99964 | 1.0046 | 0.99378 | 1.0123 | 506173.8386 | 39150.8646 | 1458.1315 | 11352.9078 | 73682.1024 | 404664.8544 | 152654.7359 | 5045.9547 | 454.5795 | 0 | 24526.7707 | 478.4023 | 23787.3433 | 24350.9886 | 443.7347 | 21358.7981 | 24226.1922 | 466.4909 | 464.3713 | 443.8948 | 504787.353 | 30155.1723 | 435.1225 | 501697.218 | 469.4085 | 530095.338 | 30365.0875 | 460.8414 | 519559.739 | 30107.8604 | 0.18208
2022-05-17 | 2022-05-17 00:00:00+00:00 | 1.0077 | 0.98173 | 0.98829 | 0.97707 | 1.0052 | 764513.7238 | 57657.9028 | 1923.696 | 16209.8104 | 112101.853 | 598633.0014 | 109098.3546 | 7549.4738 | 669.8145 | 0 | 35902.0788 | 704.8211 | 35330.2638 | 35895.1904 | 658.4943 | 35397.3273 | 35820.9856 | 687.3178 | 695.4626 | 670.7482 | 772373.235 | 41974.4638 | 653.483 | 760061.665 | 703.4487 | 801753.47 | 43285.4787 | 683.7834 | 778079.728 | 42620.0122 | 0.18726
2022-05-24 | 2022-05-24 00:00:00+00:00 | 1.0262 | 0.99487 | 1.0003 | 0.99349 | 1.0135 | 431619.7906 | 51688.9424 | 1075.6665 | 8981.487 | 94733.2147 | 375075.4124 | 134032.278 | 4418.0058 | 392.2305 | 0 | 21246.189 | 414.5553 | 20914.5546 | 21217.1391 | 377.2651 | 20928.5143 | 21094.6417 | 403.3929 | 403.273 | 379.2094 | 435007.458 | 38543.9057 | 367.6234 | 427612.76 | 406.0379 | 464230.868 | 42440.2363 | 398.0023 | 453927.813 | 41224.1129 | 0.25257
2022-05-31 | 2022-05-31 00:00:00+00:00 | 1.0228 | 0.99686 | 1.0048 | 0.99428 | 1.0126 | 532419.2096 | 41320.1739 | 1362.09 | 11671.6573 | 78051.854 | 429516.5818 | 100415.0327 | 5313.8023 | 474.3406 | 0 | 25356.0677 | 499.4754 | 24808.6102 | 25272.3476 | 464.7117 | 25096.4421 | 25235.0885 | 486.908 | 484.5705 | 466.1739 | 536453.518 | 29849.8443 | 454.3366 | 528533.49 | 489.7078 | 558216.59 | 31282.2677 | 480.8288 | 547193.315 | 30984.3627 | 0.18172

## PR
| Row 8 DAS | [5 empty] | Row 8 SAM | [5 empty] | Method 1 DAS | [5 empty] | Method 1 SAM | [5 empty] | Method 2 DAS | [5 empty] | Method 2 SAM | [5 empty] | Method 4 DAS | [5 empty] | Method 4 SAM
|  | Yf | Yr_annual | Yr_annual_bifi | PR_annual | PR_annual_bifi |  | Yf | Yr_annual | Yr_annual_bifi | PR_annual | PR_annual_bifi |  | Yf | Yr_annual | Yr_annual_bifi | PR_annual | PR_annual_bifi |  | Yf | Yr_annual | Yr_annual_bifi | PR_annual | PR_annual_bifi |  | Yf | Yr_annual | Yr_annual_bifi | PR_annual | PR_annual_bifi |  | Yf | Yr_annual | Yr_annual_bifi | PR_annual | PR_annual_bifi |  | Yf | Yr_annual | Yr_annual_bifi | PR_annual | PR_annual_bifi |  | Yf | Yr_annual | Yr_annual_bifi | PR_annual | PR_annual_bifi
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 254.9918 | 251.1181 | 265.745 | 1.0154 | 0.95954 | 2021-06-07 17:00:00-07:00 | 52.1082 | 50.9289 | 53.0299 | 1.0232 | 0.98262 | 2021-06-07 17:00:00-07:00 | 261.6327 | 246.2331 | 260.5011 | 1.0625 | 1.0043 | 2021-06-07 17:00:00-07:00 | 53.8586 | 49.9602 | 51.9763 | 1.078 | 1.0362 | 2021-06-07 17:00:00-07:00 | 261.2278 | 245.4913 | 259.7297 | 1.0641 | 1.0058 | 2021-06-07 17:00:00-07:00 | 54.0101 | 50.0978 | 52.0934 | 1.0781 | 1.0368 | 2021-06-07 17:00:00-07:00 | 266.5125 | 250.448 | 260.5007 | 1.0641 | 1.0231 | 2021-06-07 17:00:00-07:00 | 54.0101 | 50.0978 | 52.0934 | 1.0781 | 1.0368
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 243.4714 | 239.6492 | 255.3585 | 1.0159 | 0.95345 | 2021-06-14 10:00:00-07:00 | 59.3052 | 57.8981 | 59.9866 | 1.0243 | 0.98864 | 2021-06-14 10:00:00-07:00 | 251.335 | 234.9552 | 250.3039 | 1.0697 | 1.0041 | 2021-06-14 10:00:00-07:00 | 61.5827 | 57.474 | 59.5037 | 1.0715 | 1.0349 | 2021-06-14 10:00:00-07:00 | 250.6958 | 234.157 | 249.4283 | 1.0706 | 1.0051 | 2021-06-14 10:00:00-07:00 | 61.578 | 57.4699 | 59.4704 | 1.0715 | 1.0354 | 2021-06-14 10:00:00-07:00 | 255.9153 | 238.8232 | 249.6098 | 1.0716 | 1.0253 | 2021-06-14 10:00:00-07:00 | 61.578 | 57.4699 | 59.4704 | 1.0715 | 1.0354
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 125.2149 | 124.2624 | 134.2484 | 1.0077 | 0.93271 | 2021-06-21 03:15:00-07:00 | 51.3236 | 50.23 | 52.321 | 1.0218 | 0.98094 | 2021-06-21 03:15:00-07:00 | 131.8392 | 121.762 | 131.5522 | 1.0828 | 1.0022 | 2021-06-21 03:15:00-07:00 | 53.4455 | 49.5924 | 51.6227 | 1.0777 | 1.0353 | 2021-06-21 03:15:00-07:00 | 133.2043 | 123.1069 | 132.8778 | 1.082 | 1.0025 | 2021-06-21 03:15:00-07:00 | 53.5441 | 49.6776 | 51.6815 | 1.0778 | 1.036 | 2021-06-21 03:15:00-07:00 | 133.6469 | 123.5568 | 131.3783 | 1.0817 | 1.0173 | 2021-06-21 03:15:00-07:00 | 53.5441 | 49.6776 | 51.6815 | 1.0778 | 1.036
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 173.9205 | 172.7645 | 184.8447 | 1.0067 | 0.9409 | 2021-06-29 17:45:00-07:00 | 47.1897 | 46.2583 | 48.2739 | 1.0201 | 0.97754 | 2021-06-29 17:45:00-07:00 | 181.2577 | 169.7072 | 181.4589 | 1.0681 | 0.99889 | 2021-06-29 17:45:00-07:00 | 48.9359 | 45.2268 | 47.1786 | 1.082 | 1.0372 | 2021-06-29 17:45:00-07:00 | 181.1288 | 169.4194 | 181.106 | 1.0691 | 1.0001 | 2021-06-29 17:45:00-07:00 | 48.9919 | 45.2921 | 47.1714 | 1.0817 | 1.0386 | 2021-06-29 17:45:00-07:00 | 184.6971 | 172.5094 | 181.7758 | 1.0706 | 1.0161 | 2021-06-29 17:45:00-07:00 | 48.9919 | 45.2921 | 47.1714 | 1.0817 | 1.0386
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 202.0439 | 199.3482 | 212.3847 | 1.0135 | 0.95131 | 2021-07-07 14:30:00-07:00 | 61.0772 | 59.213 | 61.3157 | 1.0315 | 0.99611 | 2021-07-07 14:30:00-07:00 | 210.406 | 197.247 | 209.9063 | 1.0667 | 1.0024 | 2021-07-07 14:30:00-07:00 | 62.976 | 58.351 | 60.3497 | 1.0793 | 1.0435 | 2021-07-07 14:30:00-07:00 | 210.7554 | 197.1449 | 209.9336 | 1.069 | 1.0039 | 2021-07-07 14:30:00-07:00 | 63.4193 | 58.745 | 60.766 | 1.0796 | 1.0437 | 2021-07-07 14:30:00-07:00 | 213.4621 | 198.9991 | 208.5234 | 1.0727 | 1.0237 | 2021-07-07 14:30:00-07:00 | 63.4193 | 58.745 | 60.766 | 1.0796 | 1.0437
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 194.1631 | 191.581 | 205.2704 | 1.0135 | 0.94589 | 2021-07-14 07:30:00-07:00 | 61.6916 | 59.9198 | 61.9415 | 1.0296 | 0.99597 | 2021-07-14 07:30:00-07:00 | 198.8966 | 184.891 | 198.0332 | 1.0758 | 1.0044 | 2021-07-14 07:30:00-07:00 | 63.8841 | 59.444 | 61.4067 | 1.0747 | 1.0403 | 2021-07-14 07:30:00-07:00 | 199.8905 | 185.851 | 198.8915 | 1.0755 | 1.005 | 2021-07-14 07:30:00-07:00 | 63.9797 | 59.527 | 61.4562 | 1.0748 | 1.0411 | 2021-07-14 07:30:00-07:00 | 202.5857 | 187.8461 | 198.3328 | 1.0785 | 1.0214 | 2021-07-14 07:30:00-07:00 | 63.9797 | 59.527 | 61.4562 | 1.0748 | 1.0411
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 210.342 | 207.565 | 221.5882 | 1.0134 | 0.94925 | 2021-07-21 00:30:00-07:00 | 39.2377 | 38.4793 | 40.1046 | 1.0197 | 0.97838 | 2021-07-21 00:30:00-07:00 | 221.4785 | 207.4642 | 221.046 | 1.0676 | 1.002 | 2021-07-21 00:30:00-07:00 | 40.2422 | 37.2367 | 38.7572 | 1.0807 | 1.0383 | 2021-07-21 00:30:00-07:00 | 220.5804 | 206.1644 | 219.932 | 1.0699 | 1.0029 | 2021-07-21 00:30:00-07:00 | 40.5937 | 37.5602 | 39.0645 | 1.0808 | 1.0391 | 2021-07-21 00:30:00-07:00 | 220.6193 | 205.8111 | 215.3332 | 1.072 | 1.0245 | 2021-07-21 00:30:00-07:00 | 40.5937 | 37.5602 | 39.0645 | 1.0808 | 1.0391
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 188.6029 | 186.0743 | 199.1092 | 1.0136 | 0.94723 | 2021-07-28 13:30:00-07:00 | 52.4329 | 51.0462 | 52.8934 | 1.0272 | 0.99129 | 2021-07-28 13:30:00-07:00 | 196.8217 | 183.7929 | 196.3369 | 1.0709 | 1.0025 | 2021-07-28 13:30:00-07:00 | 54.8594 | 50.998 | 52.7894 | 1.0757 | 1.0392 | 2021-07-28 13:30:00-07:00 | 198.3421 | 184.9446 | 197.634 | 1.0724 | 1.0036 | 2021-07-28 13:30:00-07:00 | 54.8363 | 50.9565 | 52.7679 | 1.0761 | 1.0392 | 2021-07-28 13:30:00-07:00 | 196.5997 | 182.9043 | 192.1622 | 1.0749 | 1.0231 | 2021-07-28 13:30:00-07:00 | 54.8363 | 50.9565 | 52.7679 | 1.0761 | 1.0392
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 166.5619 | 164.9673 | 176.9998 | 1.0097 | 0.94103 | 2021-08-04 06:45:00-07:00 | 41.2228 | 40.316 | 42.0214 | 1.0225 | 0.981 | 2021-08-04 06:45:00-07:00 | 172.1333 | 159.6998 | 171.4899 | 1.0779 | 1.0038 | 2021-08-04 06:45:00-07:00 | 43.145 | 39.78 | 41.4671 | 1.0846 | 1.0405 | 2021-08-04 06:45:00-07:00 | 173.3103 | 160.8693 | 172.512 | 1.0773 | 1.0046 | 2021-08-04 06:45:00-07:00 | 43.2382 | 39.8733 | 41.5169 | 1.0844 | 1.0415 | 2021-08-04 06:45:00-07:00 | 174.7571 | 162.3608 | 171.5367 | 1.0764 | 1.0188 | 2021-08-04 06:45:00-07:00 | 43.2382 | 39.8733 | 41.5169 | 1.0844 | 1.0415
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 206.4861 | 203.8471 | 217.5949 | 1.0129 | 0.94895 | 2021-08-10 23:45:00-07:00 | 40.8242 | 39.8727 | 41.5164 | 1.0239 | 0.98333 | 2021-08-10 23:45:00-07:00 | 217.494 | 203.6424 | 217.2473 | 1.068 | 1.0011 | 2021-08-10 23:45:00-07:00 | 41.8302 | 38.6404 | 40.1922 | 1.0826 | 1.0408 | 2021-08-10 23:45:00-07:00 | 216.7721 | 202.7433 | 216.1697 | 1.0692 | 1.0028 | 2021-08-10 23:45:00-07:00 | 41.9145 | 38.7262 | 40.246 | 1.0823 | 1.0415 | 2021-08-10 23:45:00-07:00 | 217.0349 | 201.7663 | 212.4717 | 1.0757 | 1.0215 | 2021-08-10 23:45:00-07:00 | 41.9145 | 38.7262 | 40.246 | 1.0823 | 1.0415
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 177.2983 | 176.3541 | 188.3166 | 1.0054 | 0.94149 | 2021-08-17 16:45:00-07:00 | 45.6907 | 44.6122 | 46.4669 | 1.0242 | 0.9833 | 2021-08-17 16:45:00-07:00 | 185.7 | 175.1482 | 186.7908 | 1.0602 | 0.99416 | 2021-08-17 16:45:00-07:00 | 46.7811 | 43.3172 | 45.0599 | 1.08 | 1.0382 | 2021-08-17 16:45:00-07:00 | 185.5706 | 174.8625 | 186.4283 | 1.0612 | 0.9954 | 2021-08-17 16:45:00-07:00 | 47.5776 | 44.056 | 45.8152 | 1.0799 | 1.0385 | 2021-08-17 16:45:00-07:00 | 186.4766 | 175.1068 | 183.3224 | 1.0649 | 1.0172 | 2021-08-17 16:45:00-07:00 | 47.5776 | 44.056 | 45.8152 | 1.0799 | 1.0385
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 223.2556 | 222.0916 | 235.8814 | 1.0052 | 0.94647 | 2021-08-24 13:30:00-07:00 | 44.3431 | 43.2634 | 45.009 | 1.025 | 0.98521 | 2021-08-24 13:30:00-07:00 | 231.2563 | 219.5759 | 232.9335 | 1.0532 | 0.9928 | 2021-08-24 13:30:00-07:00 | 46.5771 | 43.0079 | 44.7273 | 1.083 | 1.0414 | 2021-08-24 13:30:00-07:00 | 231.3011 | 219.2599 | 232.7211 | 1.0549 | 0.9939 | 2021-08-24 13:30:00-07:00 | 46.5545 | 42.9867 | 44.6533 | 1.083 | 1.0426 | 2021-08-24 13:30:00-07:00 | 235.3236 | 222.9128 | 231.2081 | 1.0557 | 1.0178 | 2021-08-24 13:30:00-07:00 | 46.5545 | 42.9867 | 44.6533 | 1.083 | 1.0426
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 161.6388 | 161.9414 | 173.9787 | 0.99813 | 0.92907 | 2021-08-31 06:30:00-07:00 | 41.8154 | 40.7934 | 42.4076 | 1.0251 | 0.98604 | 2021-08-31 06:30:00-07:00 | 160.5344 | 150.84 | 161.9619 | 1.0643 | 0.99119 | 2021-08-31 06:30:00-07:00 | 43.0461 | 39.7144 | 41.2624 | 1.0839 | 1.0432 | 2021-08-31 06:30:00-07:00 | 162.8562 | 153.1547 | 164.305 | 1.0633 | 0.99118 | 2021-08-31 06:30:00-07:00 | 43.1798 | 39.849 | 41.346 | 1.0836 | 1.0444 | 2021-08-31 06:30:00-07:00 | 168.6284 | 158.28 | 166.0332 | 1.0654 | 1.0156 | 2021-08-31 06:30:00-07:00 | 43.1798 | 39.849 | 41.346 | 1.0836 | 1.0444
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 210.708 | 208.7601 | 223.123 | 1.0093 | 0.94436 | 2021-09-06 23:30:00-07:00 | 45.9608 | 44.7516 | 46.3758 | 1.027 | 0.99105 | 2021-09-06 23:30:00-07:00 | 221.7295 | 207.9482 | 222.0591 | 1.0663 | 0.99852 | 2021-09-06 23:30:00-07:00 | 47.968 | 44.4753 | 46.0817 | 1.0785 | 1.0409 | 2021-09-06 23:30:00-07:00 | 219.8418 | 206.1832 | 220.1607 | 1.0662 | 0.99855 | 2021-09-06 23:30:00-07:00 | 48.0526 | 44.5584 | 46.0973 | 1.0784 | 1.0424 | 2021-09-06 23:30:00-07:00 | 220.8985 | 206.6715 | 217.0461 | 1.0688 | 1.0177 | 2021-09-06 23:30:00-07:00 | 48.0526 | 44.5584 | 46.0973 | 1.0784 | 1.0424
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 166.9204 | 166.262 | 178.3975 | 1.004 | 0.93567 | 2021-09-13 17:00:00-07:00 | 51.3158 | 49.6763 | 51.2828 | 1.033 | 1.0006 | 2021-09-13 17:00:00-07:00 | 170.9691 | 160.5621 | 172.1457 | 1.0648 | 0.99316 | 2021-09-13 17:00:00-07:00 | 52.9287 | 49.0553 | 50.5708 | 1.079 | 1.0466 | 2021-09-13 17:00:00-07:00 | 172.2228 | 161.7643 | 173.4316 | 1.0647 | 0.99303 | 2021-09-13 17:00:00-07:00 | 53.4273 | 49.4815 | 51.0415 | 1.0797 | 1.0467 | 2021-09-13 17:00:00-07:00 | 178.2573 | 167.24 | 175.7446 | 1.0659 | 1.0143 | 2021-09-13 17:00:00-07:00 | 53.467 | 49.5105 | 51.0861 | 1.0799 | 1.0466
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 193.5287 | 192.1965 | 205.4924 | 1.0069 | 0.94178 | 2021-09-20 10:00:00-07:00 | 19.6172 | 19.3486 | 20.398 | 1.0139 | 0.96173 | 2021-09-20 10:00:00-07:00 | 198.2015 | 186.1438 | 198.942 | 1.0648 | 0.99628 | 2021-09-20 10:00:00-07:00 | 20.9556 | 19.2577 | 20.2333 | 1.0882 | 1.0357 | 2021-09-20 10:00:00-07:00 | 200.2489 | 188.0835 | 200.878 | 1.0647 | 0.99687 | 2021-09-20 10:00:00-07:00 | 21.0894 | 19.3142 | 20.3702 | 1.0919 | 1.0353 | 2021-09-20 10:00:00-07:00 | 203.126 | 190.6606 | 199.5422 | 1.0654 | 1.018 | 2021-09-20 10:00:00-07:00 | 21.0894 | 19.3142 | 20.3702 | 1.0919 | 1.0353
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 133.4646 | 132.5225 | 142.0901 | 1.0071 | 0.9393 | 2021-09-28 01:30:00-07:00 | 43.2784 | 42.1593 | 43.9018 | 1.0265 | 0.9858 | 2021-09-28 01:30:00-07:00 | 134.5127 | 125.0527 | 134.1203 | 1.0756 | 1.0029 | 2021-09-28 01:30:00-07:00 | 46.7346 | 43.3721 | 44.8257 | 1.0775 | 1.0426 | 2021-09-28 01:30:00-07:00 | 134.8233 | 125.5924 | 134.4289 | 1.0735 | 1.0029 | 2021-09-28 01:30:00-07:00 | 45.5526 | 42.0555 | 43.7669 | 1.0832 | 1.0408 | 2021-09-28 01:30:00-07:00 | 141.7415 | 131.8732 | 139.3303 | 1.0748 | 1.0173 | 2021-09-28 01:30:00-07:00 | 45.5526 | 42.0555 | 43.7669 | 1.0832 | 1.0408
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 173.7814 | 173.2265 | 185.1096 | 1.0032 | 0.9388 | 2021-10-04 18:30:00-07:00 | 33.4144 | 32.6154 | 33.7492 | 1.0245 | 0.99008 | 2021-10-04 18:30:00-07:00 | 181.9459 | 170.8907 | 182.2459 | 1.0647 | 0.99835 | 2021-10-04 18:30:00-07:00 | 34.9397 | 32.4299 | 33.5692 | 1.0774 | 1.0408 | 2021-10-04 18:30:00-07:00 | 181.593 | 170.1296 | 181.6338 | 1.0674 | 0.99978 | 2021-10-04 18:30:00-07:00 | 34.9868 | 32.4673 | 33.5489 | 1.0776 | 1.0429 | 2021-10-04 18:30:00-07:00 | 182.2409 | 170.344 | 178.7454 | 1.0698 | 1.0196 | 2021-10-04 18:30:00-07:00 | 34.9868 | 32.4673 | 33.5489 | 1.0776 | 1.0429
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 147.9698 | 147.7551 | 158.0934 | 1.0015 | 0.93596 | 2021-10-11 11:30:00-07:00 | 26.6343 | 26.0274 | 26.8371 | 1.0233 | 0.99244 | 2021-10-11 11:30:00-07:00 | 154.6784 | 145.4238 | 155.3139 | 1.0636 | 0.99591 | 2021-10-11 11:30:00-07:00 | 27.7674 | 25.9071 | 26.7446 | 1.0718 | 1.0382 | 2021-10-11 11:30:00-07:00 | 155.4805 | 146.0843 | 156.1572 | 1.0643 | 0.99567 | 2021-10-11 11:30:00-07:00 | 27.8952 | 26.0134 | 26.8167 | 1.0723 | 1.0402 | 2021-10-11 11:30:00-07:00 | 156.8646 | 147.1307 | 155.1411 | 1.0662 | 1.0111 | 2021-10-11 11:30:00-07:00 | 27.8952 | 26.0134 | 26.8167 | 1.0723 | 1.0402
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 140.9565 | 140.3646 | 149.9241 | 1.0042 | 0.94019 | 2021-10-18 04:30:00-07:00 | 34.0699 | 33.3794 | 34.4809 | 1.0207 | 0.98808 | 2021-10-18 04:30:00-07:00 | 147.427 | 137.9747 | 147.4475 | 1.0685 | 0.99986 | 2021-10-18 04:30:00-07:00 | 35.4665 | 33.0479 | 34.1486 | 1.0732 | 1.0386 | 2021-10-18 04:30:00-07:00 | 147.2361 | 137.9955 | 147.2903 | 1.067 | 0.99963 | 2021-10-18 04:30:00-07:00 | 35.5889 | 33.1679 | 34.2223 | 1.073 | 1.0399 | 2021-10-18 04:30:00-07:00 | 152.9486 | 142.8818 | 150.9866 | 1.0705 | 1.013 | 2021-10-18 04:30:00-07:00 | 35.5889 | 33.1679 | 34.2223 | 1.073 | 1.0399
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 101.8071 | 101.7566 | 108.7989 | 1.0005 | 0.93574 | 2021-10-27 16:30:00-07:00 | 36.7357 | 35.8085 | 36.8172 | 1.0259 | 0.99779 | 2021-10-27 16:30:00-07:00 | 108.6289 | 101.7344 | 108.6797 | 1.0678 | 0.99953 | 2021-10-27 16:30:00-07:00 | 38.2514 | 35.6261 | 36.6583 | 1.0737 | 1.0435 | 2021-10-27 16:30:00-07:00 | 108.7846 | 101.9707 | 108.7424 | 1.0668 | 1.0004 | 2021-10-27 16:30:00-07:00 | 38.4412 | 35.8521 | 36.8134 | 1.0722 | 1.0442 | 2021-10-27 16:30:00-07:00 | 110.9853 | 103.9023 | 109.3358 | 1.0682 | 1.0151 | 2021-10-27 16:30:00-07:00 | 38.4412 | 35.8521 | 36.8134 | 1.0722 | 1.0442
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 87.3788 | 87.8189 | 94.1466 | 0.99499 | 0.92811 | 2021-11-03 09:30:00-07:00 | 37.8971 | 36.9252 | 37.9742 | 1.0263 | 0.99797 | 2021-11-03 09:30:00-07:00 | 92.7833 | 86.6218 | 92.8518 | 1.0711 | 0.99926 | 2021-11-03 09:30:00-07:00 | 39.4925 | 36.842 | 37.8555 | 1.0719 | 1.0432 | 2021-11-03 09:30:00-07:00 | 93.4509 | 87.2703 | 93.4222 | 1.0708 | 1.0003 | 2021-11-03 09:30:00-07:00 | 39.6718 | 36.9905 | 38.0033 | 1.0725 | 1.0439 | 2021-11-03 09:30:00-07:00 | 94.3201 | 87.927 | 93.0892 | 1.0727 | 1.0132 | 2021-11-03 09:30:00-07:00 | 39.6718 | 36.9905 | 38.0033 | 1.0725 | 1.0439
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 112.6072 | 112.5579 | 120.8102 | 1.0004 | 0.9321 | 2021-11-10 02:30:00-07:00 | 27.0297 | 26.4398 | 27.3625 | 1.0223 | 0.98784 | 2021-11-10 02:30:00-07:00 | 122.2863 | 113.9396 | 122.4328 | 1.0733 | 0.9988 | 2021-11-10 02:30:00-07:00 | 27.5401 | 25.5149 | 26.4123 | 1.0794 | 1.0427 | 2021-11-10 02:30:00-07:00 | 122.4731 | 114.2611 | 122.5157 | 1.0719 | 0.99965 | 2021-11-10 02:30:00-07:00 | 28.1091 | 26.0524 | 26.928 | 1.0789 | 1.0439 | 2021-11-10 02:30:00-07:00 | 124.5845 | 116.0614 | 123.4705 | 1.0734 | 1.009 | 2021-11-10 02:30:00-07:00 | 28.0497 | 25.9953 | 26.8726 | 1.079 | 1.0438
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 79.6244 | 80.2891 | 86.7572 | 0.99172 | 0.91779 | 2021-11-16 19:30:00-07:00 | 17.9537 | 17.7573 | 18.5558 | 1.0111 | 0.96755 | 2021-11-16 19:30:00-07:00 | 85.6365 | 79.5685 | 86.0132 | 1.0763 | 0.99562 | 2021-11-16 19:30:00-07:00 | 18.7211 | 17.3091 | 18.0939 | 1.0816 | 1.0347 | 2021-11-16 19:30:00-07:00 | 87.6477 | 81.4865 | 87.9921 | 1.0756 | 0.99609 | 2021-11-16 19:30:00-07:00 | 19.1044 | 17.7052 | 18.4216 | 1.079 | 1.0371 | 2021-11-16 19:30:00-07:00 | 89.5851 | 83.1584 | 89.288 | 1.0773 | 1.0033 | 2021-11-16 19:30:00-07:00 | 19.1044 | 17.7052 | 18.4216 | 1.079 | 1.0371
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 100.1029 | 100.5416 | 108.2817 | 0.99564 | 0.92447 | 2021-11-23 13:00:00-07:00 | 25.2454 | 25.0079 | 27.9458 | 1.0095 | 0.90337 | 2021-11-23 13:00:00-07:00 | 104.272 | 97.047 | 104.4102 | 1.0744 | 0.99868 | 2021-11-23 13:00:00-07:00 | 27.8251 | 25.0349 | 27.1304 | 1.1115 | 1.0256 | 2021-11-23 13:00:00-07:00 | 104.8623 | 97.4865 | 104.9268 | 1.0757 | 0.99939 | 2021-11-23 13:00:00-07:00 | 27.9511 | 24.7994 | 27.329 | 1.1271 | 1.0228 | 2021-11-23 13:00:00-07:00 | 107.4644 | 99.7046 | 106.8565 | 1.0778 | 1.0057 | 2021-11-23 13:00:00-07:00 | 27.9511 | 24.7994 | 27.329 | 1.1271 | 1.0228
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 111.5819 | 111.612 | 119.804 | 0.99973 | 0.93137 | 2021-11-30 06:00:00-07:00 | 24.594 | 24.2355 | 26.1891 | 1.0148 | 0.93909 | 2021-11-30 06:00:00-07:00 | 114.8907 | 107.0244 | 114.477 | 1.0735 | 1.0036 | 2021-11-30 06:00:00-07:00 | 26.7932 | 24.5474 | 25.8745 | 1.0915 | 1.0355 | 2021-11-30 06:00:00-07:00 | 116.123 | 107.7941 | 115.4754 | 1.0773 | 1.0056 | 2021-11-30 06:00:00-07:00 | 27.0226 | 24.2308 | 26.2012 | 1.1152 | 1.0313 | 2021-11-30 06:00:00-07:00 | 119.3273 | 110.475 | 118.6394 | 1.0801 | 1.0058 | 2021-11-30 06:00:00-07:00 | 27.0226 | 24.2308 | 26.2012 | 1.1152 | 1.0313
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 78.0176 | 78.3872 | 84.6187 | 0.99528 | 0.92199 | 2021-12-06 23:15:00-07:00 | 16.7129 | 16.4832 | 17.7424 | 1.0139 | 0.94197 | 2021-12-06 23:15:00-07:00 | 79.8284 | 74.2707 | 80.5065 | 1.0748 | 0.99158 | 2021-12-06 23:15:00-07:00 | 17.7655 | 16.4163 | 17.1825 | 1.0822 | 1.0339 | 2021-12-06 23:15:00-07:00 | 83.2027 | 76.8056 | 83.3829 | 1.0833 | 0.99784 | 2021-12-06 23:15:00-07:00 | 18.6887 | 17.0359 | 18.1419 | 1.097 | 1.0301 | 2021-12-06 23:15:00-07:00 | 79.791 | 73.7641 | 80.0904 | 1.0817 | 0.99626 | 2021-12-06 23:15:00-07:00 | 18.6887 | 17.0359 | 18.1419 | 1.097 | 1.0301
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 93.0873 | 93.1123 | 100.3755 | 0.99973 | 0.92739 | 2021-12-13 16:15:00-07:00 | 22.9923 | 22.8867 | 26.1425 | 1.0046 | 0.8795 | 2021-12-13 16:15:00-07:00 | 97.4194 | 90.5837 | 97.8331 | 1.0755 | 0.99577 | 2021-12-13 16:15:00-07:00 | 26.4897 | 22.9502 | 26.0655 | 1.1542 | 1.0163 | 2021-12-13 16:15:00-07:00 | 99.7482 | 92.1255 | 99.7506 | 1.0827 | 0.99998 | 2021-12-13 16:15:00-07:00 | 26.3474 | 22.6712 | 25.9371 | 1.1622 | 1.0158 | 2021-12-13 16:15:00-07:00 | 97.5629 | 90.2274 | 97.744 | 1.0813 | 0.99815 | 2021-12-13 16:15:00-07:00 | 26.3474 | 22.6712 | 25.9371 | 1.1622 | 1.0158
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 104.1474 | 104.4097 | 111.8276 | 0.99749 | 0.93132 | 2021-12-20 09:15:00-07:00 | 21.2394 | 21.0416 | 22.9196 | 1.0094 | 0.92669 | 2021-12-20 09:15:00-07:00 | 108.5074 | 101.3919 | 108.4515 | 1.0702 | 1.0005 | 2021-12-20 09:15:00-07:00 | 22.6096 | 20.7684 | 21.9126 | 1.0887 | 1.0318 | 2021-12-20 09:15:00-07:00 | 108.6648 | 101.4905 | 108.5106 | 1.0707 | 1.0014 | 2021-12-20 09:15:00-07:00 | 23.309 | 20.9852 | 22.7218 | 1.1107 | 1.0258 | 2021-12-20 09:15:00-07:00 | 110.8975 | 103.5531 | 110.9573 | 1.0709 | 0.99946 | 2021-12-20 09:15:00-07:00 | 23.309 | 20.9852 | 22.7218 | 1.1107 | 1.0258
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 90.1466 | 90.2764 | 96.992 | 0.99856 | 0.92942 | 2021-12-27 02:45:00-07:00 | 21.1935 | 21.1352 | 21.8769 | 1.0028 | 0.96876 | 2021-12-27 02:45:00-07:00 | 93.0008 | 86.5546 | 92.9637 | 1.0745 | 1.0004 | 2021-12-27 02:45:00-07:00 | 22.5001 | 21.3211 | 22.112 | 1.0553 | 1.0176 | 2021-12-27 02:45:00-07:00 | 93.36 | 86.9256 | 93.1906 | 1.074 | 1.0018 | 2021-12-27 02:45:00-07:00 | 22.3241 | 21.1864 | 21.922 | 1.0537 | 1.0183 | 2021-12-27 02:45:00-07:00 | 96.9848 | 90.1914 | 97.3803 | 1.0753 | 0.99594 | 2021-12-27 02:45:00-07:00 | 22.3241 | 21.1864 | 21.922 | 1.0537 | 1.0183
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 66.3155 | 67.7905 | 78.8048 | 0.97824 | 0.84152 | 2022-01-02 19:45:00-07:00 | 18.2569 | 18.0871 | 20.1153 | 1.0094 | 0.90761 | 2022-01-02 19:45:00-07:00 | 81.9062 | 71.2628 | 83.6783 | 1.1494 | 0.97882 | 2022-01-02 19:45:00-07:00 | 21.0523 | 18.8388 | 20.5316 | 1.1175 | 1.0254 | 2022-01-02 19:45:00-07:00 | 85.8834 | 74.3167 | 89.2147 | 1.1556 | 0.96266 | 2022-01-02 19:45:00-07:00 | 20.1939 | 17.9559 | 19.7381 | 1.1246 | 1.0231 | 2022-01-02 19:45:00-07:00 | 89.1914 | 74.4639 | 90.4318 | 1.1978 | 0.98628 | 2022-01-02 19:45:00-07:00 | 20.1939 | 17.9559 | 19.7381 | 1.1246 | 1.0231
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 92.8922 | 93.1738 | 105.7827 | 0.99698 | 0.87814 | 2022-01-09 13:00:00-07:00 | 24.1288 | 23.8662 | 26.7667 | 1.011 | 0.90145 | 2022-01-09 13:00:00-07:00 | 104.9282 | 93.8855 | 106.8021 | 1.1176 | 0.98246 | 2022-01-09 13:00:00-07:00 | 27.3973 | 24.144 | 26.7012 | 1.1347 | 1.0261 | 2022-01-09 13:00:00-07:00 | 107.5627 | 95.7609 | 109.265 | 1.1232 | 0.98442 | 2022-01-09 13:00:00-07:00 | 27.3897 | 23.9198 | 26.7817 | 1.1451 | 1.0227 | 2022-01-09 13:00:00-07:00 | 108.286 | 94.0351 | 108.4909 | 1.1515 | 0.99811 | 2022-01-09 13:00:00-07:00 | 27.3897 | 23.9198 | 26.7817 | 1.1451 | 1.0227
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 55.9978 | 55.9897 | 61.7367 | 1.0001 | 0.90704 | 2022-01-16 06:00:00-07:00 | 19.7109 | 19.526 | 20.6305 | 1.0095 | 0.95542 | 2022-01-16 06:00:00-07:00 | 61.1296 | 55.7148 | 61.0857 | 1.0972 | 1.0007 | 2022-01-16 06:00:00-07:00 | 20.5221 | 19.0746 | 19.9443 | 1.0759 | 1.029 | 2022-01-16 06:00:00-07:00 | 60.1156 | 55.0075 | 59.9195 | 1.0929 | 1.0033 | 2022-01-16 06:00:00-07:00 | 20.6942 | 19.2616 | 20.1046 | 1.0744 | 1.0293 | 2022-01-16 06:00:00-07:00 | 61.792 | 55.9007 | 62.193 | 1.1054 | 0.99355 | 2022-01-16 06:00:00-07:00 | 20.6942 | 19.2616 | 20.1046 | 1.0744 | 1.0293
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 78.2506 | 78.8374 | 87.6703 | 0.99256 | 0.89256 | 2022-01-22 23:00:00-07:00 | 17.9149 | 18.0115 | 18.9025 | 0.99464 | 0.94775 | 2022-01-22 23:00:00-07:00 | 91.0279 | 84.2427 | 92.68 | 1.0805 | 0.98217 | 2022-01-22 23:00:00-07:00 | 18.7606 | 17.6829 | 18.5776 | 1.0609 | 1.0099 | 2022-01-22 23:00:00-07:00 | 91.214 | 83.7767 | 92.3076 | 1.0888 | 0.98815 | 2022-01-22 23:00:00-07:00 | 19.1403 | 18.0539 | 18.9155 | 1.0602 | 1.0119 | 2022-01-22 23:00:00-07:00 | 90.7539 | 83.0696 | 90.7869 | 1.0925 | 0.99964 | 2022-01-22 23:00:00-07:00 | 19.1403 | 18.0539 | 18.9155 | 1.0602 | 1.0119
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 101.8595 | 102.1265 | 117.3674 | 0.99739 | 0.86787 | 2022-01-29 16:00:00-07:00 | 19.9013 | 19.7707 | 21.2337 | 1.0066 | 0.93725 | 2022-01-29 16:00:00-07:00 | 119.2712 | 107.5982 | 122.0992 | 1.1085 | 0.97684 | 2022-01-29 16:00:00-07:00 | 21.2952 | 19.909 | 20.7602 | 1.0696 | 1.0258 | 2022-01-29 16:00:00-07:00 | 123.8462 | 110.6078 | 126.9026 | 1.1197 | 0.97592 | 2022-01-29 16:00:00-07:00 | 21.1726 | 19.6176 | 20.6607 | 1.0793 | 1.0248 | 2022-01-29 16:00:00-07:00 | 121.6763 | 107.574 | 122.6595 | 1.1311 | 0.99198 | 2022-01-29 16:00:00-07:00 | 21.1726 | 19.6176 | 20.6607 | 1.0793 | 1.0248
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 128.8811 | 128.4565 | 149.5153 | 1.0033 | 0.86199 | 2022-02-05 09:00:00-07:00 | 21.8218 | 21.69 | 22.8766 | 1.0061 | 0.95389 | 2022-02-05 09:00:00-07:00 | 149.091 | 132.9203 | 152.9457 | 1.1217 | 0.9748 | 2022-02-05 09:00:00-07:00 | 23.7221 | 22.3259 | 23.1402 | 1.0625 | 1.0251 | 2022-02-05 09:00:00-07:00 | 148.4347 | 130.8473 | 151.0009 | 1.1344 | 0.98301 | 2022-02-05 09:00:00-07:00 | 23.1442 | 21.5854 | 22.5805 | 1.0722 | 1.025 | 2022-02-05 09:00:00-07:00 | 147.6723 | 128.3379 | 147.7647 | 1.1507 | 0.99937 | 2022-02-05 09:00:00-07:00 | 23.1442 | 21.5854 | 22.5805 | 1.0722 | 1.025
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 127.9563 | 126.9003 | 140.2152 | 1.0083 | 0.91257 | 2022-02-12 02:00:00-07:00 | 25.3681 | 25.1494 | 26.8077 | 1.0087 | 0.9463 | 2022-02-12 02:00:00-07:00 | 139.3546 | 128.7598 | 138.8824 | 1.0823 | 1.0034 | 2022-02-12 02:00:00-07:00 | 27.5031 | 25.597 | 26.8127 | 1.0745 | 1.0257 | 2022-02-12 02:00:00-07:00 | 138.4188 | 126.651 | 138.1659 | 1.0929 | 1.0018 | 2022-02-12 02:00:00-07:00 | 26.871 | 24.6925 | 26.2807 | 1.0882 | 1.0225 | 2022-02-12 02:00:00-07:00 | 140.6671 | 127.6557 | 139.5518 | 1.1019 | 1.008 | 2022-02-12 02:00:00-07:00 | 26.871 | 24.6925 | 26.2807 | 1.0882 | 1.0225
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 112.2115 | 112.0283 | 124.1513 | 1.0016 | 0.90383 | 2022-02-18 19:30:00-07:00 | 30.3904 | 30.2419 | 32.6707 | 1.0049 | 0.9302 | 2022-02-18 19:30:00-07:00 | 120.1411 | 109.86 | 121.1142 | 1.0936 | 0.99197 | 2022-02-18 19:30:00-07:00 | 33.7264 | 31.2819 | 33.0674 | 1.0781 | 1.0199 | 2022-02-18 19:30:00-07:00 | 116.987 | 108.0395 | 117.944 | 1.0828 | 0.99189 | 2022-02-18 19:30:00-07:00 | 32.665 | 30.1494 | 32.0603 | 1.0834 | 1.0189 | 2022-02-18 19:30:00-07:00 | 126.4995 | 113.0679 | 125.564 | 1.1188 | 1.0075 | 2022-02-18 19:30:00-07:00 | 32.665 | 30.1494 | 32.0603 | 1.0834 | 1.0189
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 167.0875 | 165.4832 | 180.3059 | 1.0097 | 0.92669 | 2022-02-28 08:45:00-07:00 | 46.2795 | 45.8212 | 49.4742 | 1.01 | 0.93543 | 2022-02-28 08:45:00-07:00 | 170.0324 | 159.2311 | 169.9592 | 1.0678 | 1.0004 | 2022-02-28 08:45:00-07:00 | 49.3047 | 45.3295 | 48.2049 | 1.0877 | 1.0228 | 2022-02-28 08:45:00-07:00 | 179.5849 | 164.9432 | 179.8998 | 1.0888 | 0.99825 | 2022-02-28 08:45:00-07:00 | 50.1995 | 45.8098 | 49.3708 | 1.0958 | 1.0168 | 2022-02-28 08:45:00-07:00 | 180.6543 | 165.5084 | 177.8645 | 1.0915 | 1.0157 | 2022-02-28 08:45:00-07:00 | 50.1995 | 45.8098 | 49.3708 | 1.0958 | 1.0168
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 77.7766 | 78.28 | 89.4214 | 0.99357 | 0.86978 | 2022-03-08 16:00:00-07:00 | 28.1005 | 27.9265 | 31.1462 | 1.0062 | 0.90221 | 2022-03-08 16:00:00-07:00 | 83.8291 | 75.4905 | 86.8713 | 1.1105 | 0.96498 | 2022-03-08 16:00:00-07:00 | 30.8786 | 28.0068 | 30.2023 | 1.1025 | 1.0224 | 2022-03-08 16:00:00-07:00 | 84.118 | 77.034 | 86.068 | 1.092 | 0.97734 | 2022-03-08 16:00:00-07:00 | 31.2268 | 27.5378 | 30.6972 | 1.134 | 1.0173 | 2022-03-08 16:00:00-07:00 | 82.7467 | 75.7638 | 84.3514 | 1.0922 | 0.98098 | 2022-03-08 16:00:00-07:00 | 31.2268 | 27.5378 | 30.6972 | 1.134 | 1.0173
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 160.5111 | 159.8795 | 174.4964 | 1.004 | 0.91985 | 2022-03-16 19:15:00-07:00 | 34.9821 | 34.8265 | 39.9252 | 1.0045 | 0.87619 | 2022-03-16 19:15:00-07:00 | 169.4137 | 156.9888 | 169.4837 | 1.0791 | 0.99959 | 2022-03-16 19:15:00-07:00 | 40.6552 | 34.9535 | 40.3016 | 1.1631 | 1.0088 | 2022-03-16 19:15:00-07:00 | 165.777 | 152.9658 | 165.5237 | 1.0838 | 1.0015 | 2022-03-16 19:15:00-07:00 | 40.025 | 34.6928 | 39.625 | 1.1537 | 1.0101 | 2022-03-16 19:15:00-07:00 | 174.1467 | 157.6122 | 172.8978 | 1.1049 | 1.0072 | 2022-03-16 19:15:00-07:00 | 40.025 | 34.6928 | 39.625 | 1.1537 | 1.0101
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 162.6323 | 163.0077 | 173.6926 | 0.9977 | 0.93632 | 2022-03-23 12:15:00-07:00 | 37.6787 | 37.6025 | 41.2426 | 1.002 | 0.91359 | 2022-03-23 12:15:00-07:00 | 173.0716 | 162.6424 | 172.5968 | 1.0641 | 1.0028 | 2022-03-23 12:15:00-07:00 | 41.0418 | 37.8908 | 40.4035 | 1.0832 | 1.0158 | 2022-03-23 12:15:00-07:00 | 169.9826 | 159.319 | 169.4853 | 1.0669 | 1.0029 | 2022-03-23 12:15:00-07:00 | 41.9135 | 37.8216 | 41.4936 | 1.1082 | 1.0101 | 2022-03-23 12:15:00-07:00 | 170.3805 | 159.8239 | 169.1579 | 1.0661 | 1.0072 | 2022-03-23 12:15:00-07:00 | 41.9135 | 37.8216 | 41.4936 | 1.1082 | 1.0101
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 167.2094 | 167.9203 | 177.5523 | 0.99577 | 0.94175 | 2022-03-30 05:15:00-07:00 | 50.7877 | 50.1827 | 52.0398 | 1.0121 | 0.97594 | 2022-03-30 05:15:00-07:00 | 169.3311 | 159.6058 | 168.7853 | 1.0609 | 1.0032 | 2022-03-30 05:15:00-07:00 | 53.2979 | 50.27 | 52.0071 | 1.0602 | 1.0248 | 2022-03-30 05:15:00-07:00 | 173.8718 | 164.2483 | 173.5524 | 1.0586 | 1.0018 | 2022-03-30 05:15:00-07:00 | 52.7988 | 49.8346 | 51.5627 | 1.0595 | 1.024 | 2022-03-30 05:15:00-07:00 | 176.5617 | 166.5636 | 174.7423 | 1.06 | 1.0104 | 2022-03-30 05:15:00-07:00 | 52.7988 | 49.8346 | 51.5627 | 1.0595 | 1.024
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 111.6548 | 111.922 | 118.4161 | 0.99761 | 0.9429 | 2022-04-05 22:30:00-07:00 | 32.0821 | 31.684 | 32.7837 | 1.0126 | 0.9786 | 2022-04-05 22:30:00-07:00 | 112.0533 | 105.5618 | 111.6571 | 1.0615 | 1.0035 | 2022-04-05 22:30:00-07:00 | 33.5075 | 31.539 | 32.6432 | 1.0624 | 1.0265 | 2022-04-05 22:30:00-07:00 | 113.9679 | 107.4411 | 113.6067 | 1.0607 | 1.0032 | 2022-04-05 22:30:00-07:00 | 33.9433 | 31.9468 | 33.0616 | 1.0625 | 1.0267 | 2022-04-05 22:30:00-07:00 | 119.5179 | 112.6109 | 118.1387 | 1.0613 | 1.0117 | 2022-04-05 22:30:00-07:00 | 33.9433 | 31.9468 | 33.0616 | 1.0625 | 1.0267
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 227.5647 | 226.3277 | 239.0787 | 1.0055 | 0.95184 | 2022-04-15 00:15:00-07:00 | 42.8555 | 42.6243 | 44.9146 | 1.0054 | 0.95416 | 2022-04-15 00:15:00-07:00 | 236.1316 | 223.041 | 235.3058 | 1.0587 | 1.0035 | 2022-04-15 00:15:00-07:00 | 47.582 | 45.0748 | 46.74 | 1.0556 | 1.018 | 2022-04-15 00:15:00-07:00 | 237.2429 | 223.9863 | 236.3347 | 1.0592 | 1.0038 | 2022-04-15 00:15:00-07:00 | 45.434 | 42.4605 | 44.7126 | 1.07 | 1.0161 | 2022-04-15 00:15:00-07:00 | 238.8798 | 225.2714 | 236.5488 | 1.0604 | 1.0099 | 2022-04-15 00:15:00-07:00 | 45.434 | 42.4605 | 44.7126 | 1.07 | 1.0161
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 232.7629 | 233.7947 | 246.6772 | 0.99559 | 0.94359 | 2022-04-21 17:15:00-07:00 | 42.6241 | 42.208 | 44.6673 | 1.0099 | 0.95426 | 2022-04-21 17:15:00-07:00 | 241.501 | 229.0441 | 241.5094 | 1.0544 | 0.99997 | 2022-04-21 17:15:00-07:00 | 45.3097 | 42.5659 | 44.361 | 1.0645 | 1.0214 | 2022-04-21 17:15:00-07:00 | 240.8988 | 228.3747 | 240.7171 | 1.0548 | 1.0008 | 2022-04-21 17:15:00-07:00 | 44.7404 | 41.5124 | 43.8386 | 1.0778 | 1.0206 | 2022-04-21 17:15:00-07:00 | 249.4521 | 236.1856 | 246.0447 | 1.0562 | 1.0138 | 2022-04-21 17:15:00-07:00 | 44.7404 | 41.5124 | 43.8386 | 1.0778 | 1.0206
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 197.527 | 199.3091 | 211.3698 | 0.99106 | 0.93451 | 2022-04-28 10:30:00-07:00 | 52.1953 | 51.2516 | 57.6659 | 1.0184 | 0.90513 | 2022-04-28 10:30:00-07:00 | 208.4755 | 196.2445 | 207.8063 | 1.0623 | 1.0032 | 2022-04-28 10:30:00-07:00 | 59.7777 | 52.0523 | 58.5884 | 1.1484 | 1.0203 | 2022-04-28 10:30:00-07:00 | 206.2471 | 193.7073 | 205.24 | 1.0647 | 1.0049 | 2022-04-28 10:30:00-07:00 | 58.1669 | 50.8798 | 56.874 | 1.1432 | 1.0227 | 2022-04-28 10:30:00-07:00 | 214.9676 | 201.7193 | 212.5297 | 1.0657 | 1.0115 | 2022-04-28 10:30:00-07:00 | 58.1669 | 50.8798 | 56.874 | 1.1432 | 1.0227
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 156.9776 | 156.7284 | 166.5522 | 1.0016 | 0.94251 | 2022-05-05 03:30:00-07:00 | 45.8361 | 45.1519 | 47.8086 | 1.0152 | 0.95874 | 2022-05-05 03:30:00-07:00 | 160.9399 | 150.3874 | 159.8835 | 1.0702 | 1.0066 | 2022-05-05 03:30:00-07:00 | 49.3455 | 46.0122 | 48.0329 | 1.0724 | 1.0273 | 2022-05-05 03:30:00-07:00 | 161.1899 | 150.6672 | 160.0733 | 1.0698 | 1.007 | 2022-05-05 03:30:00-07:00 | 48.8565 | 44.9697 | 47.5833 | 1.0864 | 1.0268 | 2022-05-05 03:30:00-07:00 | 166.9552 | 156.2734 | 165.3366 | 1.0684 | 1.0098 | 2022-05-05 03:30:00-07:00 | 48.8565 | 44.9697 | 47.5833 | 1.0864 | 1.0268
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 277.5976 | 274.9733 | 290.3972 | 1.0095 | 0.95592 | 2022-05-11 20:30:00-07:00 | 46.288 | 45.5492 | 47.2553 | 1.0162 | 0.97953 | 2022-05-11 20:30:00-07:00 | 283.3252 | 268.4181 | 283.358 | 1.0555 | 0.99988 | 2022-05-11 20:30:00-07:00 | 48.3933 | 45.3702 | 47.0796 | 1.0666 | 1.0279 | 2022-05-11 20:30:00-07:00 | 283.321 | 268.1039 | 282.9909 | 1.0568 | 1.0012 | 2022-05-11 20:30:00-07:00 | 48.3877 | 45.3668 | 47.0309 | 1.0666 | 1.0288 | 2022-05-11 20:30:00-07:00 | 289.6394 | 273.7888 | 285.0846 | 1.0579 | 1.016 | 2022-05-11 20:30:00-07:00 | 48.3877 | 45.3668 | 47.0309 | 1.0666 | 1.0288
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 183.5385 | 181.9536 | 197.1805 | 1.0087 | 0.93081 | 2022-05-18 13:45:00-07:00 | 39.5483 | 39.2309 | 43.3781 | 1.0081 | 0.91171 | 2022-05-18 13:45:00-07:00 | 189.2202 | 176.1688 | 189.3556 | 1.0741 | 0.99928 | 2022-05-18 13:45:00-07:00 | 44.682 | 39.6591 | 44.0358 | 1.1267 | 1.0147 | 2022-05-18 13:45:00-07:00 | 189.9159 | 176.3804 | 189.6265 | 1.0767 | 1.0015 | 2022-05-18 13:45:00-07:00 | 44.1429 | 39.3358 | 43.4523 | 1.1222 | 1.0159 | 2022-05-18 13:45:00-07:00 | 200.9647 | 185.6297 | 199.2694 | 1.0826 | 1.0085 | 2022-05-18 13:45:00-07:00 | 44.1429 | 39.3358 | 43.4523 | 1.1222 | 1.0159
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 193.283 | 190.7918 | 206.8203 | 1.0131 | 0.93455 | 2022-05-25 07:15:00-07:00 | 53.719 | 52.943 | 55.2123 | 1.0147 | 0.97295 | 2022-05-25 07:15:00-07:00 | 196.8112 | 180.6653 | 195.9912 | 1.0894 | 1.0042 | 2022-05-25 07:15:00-07:00 | 57.2852 | 53.3735 | 55.9159 | 1.0733 | 1.0245 | 2022-05-25 07:15:00-07:00 | 200.0514 | 184.301 | 198.1414 | 1.0855 | 1.0096 | 2022-05-25 07:15:00-07:00 | 56.3386 | 52.7283 | 54.9294 | 1.0685 | 1.0257 | 2022-05-25 07:15:00-07:00 | 209.5918 | 193.0677 | 207.4088 | 1.0856 | 1.0105 | 2022-05-25 07:15:00-07:00 | 56.3386 | 52.7283 | 54.9294 | 1.0685 | 1.0257

## PR_5sigma
|  | Row 8 | Method 2A | Method 2A | Method 2B
|  | PR | PR | PR_bifi | PR_bifi
2021-06-08 | 2021-06-08 00:00:00+00:00 | 1.0178 | 1.0626 | 1.0095 | 1.0302
2021-06-15 | 2021-06-15 00:00:00+00:00 | 1.019 | 1.0655 | 1.0074 | 1.0311
2021-06-22 | 2021-06-22 00:00:00+00:00 | 1.0216 | 1.0777 | 1.0096 | 1.0333
2021-06-29 | 2021-06-29 00:00:00+00:00 | 1.0119 | 1.0774 | 1.0057 | 1.0255
2021-07-06 | 2021-07-06 00:00:00+00:00 | 1.015 | 1.0665 | 1.0061 | 1.0297
2021-07-13 | 2021-07-13 00:00:00+00:00 | 1.021 | 1.0752 | 1.0103 | 1.0326
2021-07-20 | 2021-07-20 00:00:00+00:00 | 1.0189 | 1.0706 | 1.0078 | 1.0309
2021-07-27 | 2021-07-27 00:00:00+00:00 | 1.0194 | 1.0717 | 1.0072 | 1.0306
2021-08-03 | 2021-08-03 00:00:00+00:00 | 1.0196 | 1.0749 | 1.009 | 1.0312
2021-08-10 | 2021-08-10 00:00:00+00:00 | 1.0169 | 1.0749 | 1.0073 | 1.0285
2021-08-17 | 2021-08-17 00:00:00+00:00 | 1.0162 | 1.0693 | 1.0055 | 1.0295
2021-08-24 | 2021-08-24 00:00:00+00:00 | 1.0089 | 1.0568 | 0.99664 | 1.0255
2021-08-31 | 2021-08-31 00:00:00+00:00 | 1.0083 | 1.0586 | 0.99762 | 1.0274
2021-09-07 | 2021-09-07 00:00:00+00:00 | 1.01 | 1.0668 | 1.0003 | 1.0264
2021-09-14 | 2021-09-14 00:00:00+00:00 | 1.0142 | 1.0729 | 1.0034 | 1.0267
2021-09-21 | 2021-09-21 00:00:00+00:00 | 1.0099 | 1.0649 | 0.99881 | 1.0252
2021-09-28 | 2021-09-28 00:00:00+00:00 | 1.013 | 1.0662 | 1.0031 | 1.0249
2021-10-05 | 2021-10-05 00:00:00+00:00 | 1.0103 | 1.0686 | 1.0038 | 1.0249
2021-10-12 | 2021-10-12 00:00:00+00:00 | 1.007 | 1.0669 | 1.0023 | 1.023
2021-10-19 | 2021-10-19 00:00:00+00:00 | 1.0117 | 1.0658 | 1.0036 | 1.0178
2021-10-26 | 2021-10-26 00:00:00+00:00 | 1.0106 | 1.0732 | 1.0068 | 1.0217
2021-11-02 | 2021-11-02 00:00:00+00:00 | 1.0073 | 1.0709 | 1.0066 | 1.0226
2021-11-09 | 2021-11-09 00:00:00+00:00 | 1.0048 | 1.0737 | 1.0069 | 1.022
2021-11-16 | 2021-11-16 00:00:00+00:00 | 1.0061 | 1.0755 | 1.0059 | 1.0167
2021-11-23 | 2021-11-23 00:00:00+00:00 | 1.0048 | 1.0765 | 1.0057 | 1.0165
2021-11-30 | 2021-11-30 00:00:00+00:00 | 1.0036 | 1.0836 | 1.0072 | 1.0129
2021-12-07 | 2021-12-07 00:00:00+00:00 | 1.0083 | 1.0842 | 1.0129 | 1.0116
2021-12-14 | 2021-12-14 00:00:00+00:00 | 1.0084 | 1.0895 | 1.0117 | 1.0105
2021-12-21 | 2021-12-21 00:00:00+00:00 | 1.007 | 1.0755 | 1.0079 | 1.0061
2021-12-28 | 2021-12-28 00:00:00+00:00 | 1.0042 | 1.0788 | 1.0069 | 1.0076
2022-01-04 | 2022-01-04 00:00:00+00:00 | 1.003 | 1.1144 | 0.99202 | 0.99796
2022-01-11 | 2022-01-11 00:00:00+00:00 | 1.0038 | 1.1314 | 0.9884 | 1.0052
2022-01-18 | 2022-01-18 00:00:00+00:00 | 1.0053 | 1.0983 | 1.0017 | 1.0069
2022-01-25 | 2022-01-25 00:00:00+00:00 | 1.0064 | 1.075 | 0.99908 | 1.0126
2022-02-01 | 2022-02-01 00:00:00+00:00 | 1.0152 | 1.1217 | 0.99569 | 1.0138
2022-02-08 | 2022-02-08 00:00:00+00:00 | 1.0146 | 1.1505 | 0.98393 | 1.0147
2022-02-15 | 2022-02-15 00:00:00+00:00 | 1.0126 | 1.1136 | 1.0031 | 1.0169
2022-02-22 | 2022-02-22 00:00:00+00:00 | 1.0102 | 1.1059 | 0.9955 | 1.0144
2022-03-01 | 2022-03-01 00:00:00+00:00 | 1.0083 | 1.1078 | 0.98813 | 1.0145
2022-03-08 | 2022-03-08 00:00:00+00:00 | 1.0072 | 1.0748 | 1.0035 | 1.0193
2022-03-15 | 2022-03-15 00:00:00+00:00 | 1.0087 | 1.0871 | 0.9975 | 1.013
2022-03-22 | 2022-03-22 00:00:00+00:00 | 1.012 | 1.1021 | 1.0005 | 1.0167
2022-03-29 | 2022-03-29 00:00:00+00:00 | 1.0073 | 1.0618 | 1.0106 | 1.0188
2022-04-05 | 2022-04-05 00:00:00+00:00 | 1.0032 | 1.0566 | 1.0068 | 1.0201
2022-04-12 | 2022-04-12 00:00:00+00:00 | 1.007 | 1.0612 | 1.0079 | 1.0181
2022-04-19 | 2022-04-19 00:00:00+00:00 | 1.011 | 1.0607 | 1.0077 | 1.0173
2022-04-26 | 2022-04-26 00:00:00+00:00 | 0.99727 | 1.0559 | 1.0028 | 1.0211
2022-05-03 | 2022-05-03 00:00:00+00:00 | 0.99565 | 1.0634 | 1.0083 | 1.0216
2022-05-10 | 2022-05-10 00:00:00+00:00 | 1.0114 | 1.0651 | 1.0089 | 1.0214
2022-05-17 | 2022-05-17 00:00:00+00:00 | 1.0118 | 1.0573 | 1.0029 | 1.0236
2022-05-24 | 2022-05-24 00:00:00+00:00 | 1.0194 | 1.0915 | 1.0049 | 1.0195
2022-05-31 | 2022-05-31 00:00:00+00:00 | 1.0181 | 1.0675 | 1.011 | 1.0225
2022-06-07 | 2022-06-07 00:00:00+00:00 | 1.0146 | 1.0646 | 1.0078 | 1.0232

## model_error
|  | monofacial | bifacial_baseline | method2b_tcorr | method2 | method1b (S02)
2021-06-07 | 17:00:00-07:00 | 1.5177 | 0.62634 | 1.045 | 1.1612 | 0.61151
2021-06-14 | 10:00:00-07:00 | 1.6077 | 0.51526 | 0.96863 | 1.3343 | 0.65772
2021-06-21 | 03:15:00-07:00 | 1.0558 | 0.75105 | 0.9977 | 1.1175 | 1.0577
2021-06-29 | 17:45:00-07:00 | 1.4564 | 0.7558 | 1.2519 | 1.4744 | 0.98343
2021-07-07 | 14:30:00-07:00 | 1.6937 | 0.72352 | 1.0577 | 1.3926 | 0.60833
2021-07-14 | 07:30:00-07:00 | 1.5317 | 0.61673 | 1.2666 | 1.147 | 0.91176
2021-07-21 | 00:30:00-07:00 | 1.6829 | 1.0191 | 1.3183 | 1.2634 | 0.8789
2021-07-28 | 13:30:00-07:00 | 1.3477 | 0.91066 | 1.0237 | 1.1918 | 0.70776
2021-08-04 | 06:45:00-07:00 | 1.7212 | 1.0113 | 1.2882 | 1.5711 | 1.2789
2021-08-10 | 23:45:00-07:00 | 1.4562 | 0.90059 | 1.2522 | 1.3393 | 0.79076
2021-08-17 | 16:45:00-07:00 | 1.1996 | 0.57405 | 1.0594 | 1.1582 | 0.6604
2021-08-24 | 13:30:00-07:00 | 1.1849 | 0.67772 | 1.3289 | 0.99182 | 0.73576
2021-08-31 | 06:30:00-07:00 | 1.6443 | 0.79749 | 1.0959 | 1.1888 | 0.75076
2021-09-06 | 23:30:00-07:00 | 0.96418 | 0.5177 | 1.1753 | 0.99069 | 0.96588
2021-09-13 | 17:00:00-07:00 | 1.4748 | 0.77347 | 1.0277 | 1.3972 | 0.90373
2021-09-20 | 10:00:00-07:00 | 1.9952 | 1.6554 | 0.98384 | 1.8298 | 1.043
2021-09-28 | 01:30:00-07:00 | 1.8323 | 0.86203 | 1.2163 | 1.4981 | 1.2069
2021-10-04 | 18:30:00-07:00 | 1.2154 | 0.74226 | 1.2358 | 1.0887 | 1.2244
2021-10-11 | 11:30:00-07:00 | 1.5799 | 0.63411 | 1.0621 | 1.4423 | 1.6375
2021-10-18 | 04:30:00-07:00 | 1.0752 | 0.60709 | 1.1812 | 1.0041 | 1.4672
2021-10-27 | 16:30:00-07:00 | 1.2125 | 0.74618 | 1.1706 | 1.2066 | 2.5293
2021-11-03 | 09:30:00-07:00 | 0.92364 | 0.7477 | 1.5963 | 0.84271 | 2.3784
2021-11-10 | 02:30:00-07:00 | 0.84155 | 0.93064 | 0.75554 | 0.70538 | 1.687
2021-11-16 | 19:30:00-07:00 | 0.56447 | 0.94738 | 0.83913 | 0.76095 | 1.4898
2021-11-23 | 13:00:00-07:00 | 0.73906 | 5.7335 | 0.64439 | 0.75925 | 2.516
2021-11-30 | 06:00:00-07:00 | 0.73997 | 2.29 | 0.73001 | 0.61833 | 2.4607
2021-12-06 | 23:15:00-07:00 | 0.77126 | 1.5093 | 0.64434 | 0.56446 | 1.8881
2021-12-13 | 16:15:00-07:00 | 0.55825 | 5.1886 | 0.55349 | 0.52267 | 2.0392
2021-12-20 | 09:15:00-07:00 | 0.49893 | 1.5318 | 0.51694 | 0.40462 | 1.9484
2021-12-27 | 02:45:00-07:00 | 0.52426 | 0.5531 | 0.48238 | 0.41177 | 2.1197
2022-01-02 | 19:45:00-07:00 | 0.42023 | 3.6064 | 0.63679 | 0.55425 | 5.0251
2022-01-09 | 13:00:00-07:00 | 0.84206 | 4.9416 | 0.68853 | 1.7191 | 4.2835
2022-01-16 | 06:00:00-07:00 | 0.42103 | 1.1705 | 0.65363 | 0.52452 | 2.1977
2022-01-22 | 23:00:00-07:00 | 0.57831 | 0.85366 | 1.2482 | 0.6244 | 3.7462
2022-01-29 | 16:00:00-07:00 | 0.7908 | 1.4729 | 1.0534 | 1.0141 | 5.0617
2022-02-05 | 09:00:00-07:00 | 0.57915 | 0.86003 | 0.80223 | 0.60845 | 4.085
2022-02-12 | 02:00:00-07:00 | 0.76029 | 0.78133 | 0.8483 | 0.70292 | 1.9004
2022-02-18 | 19:30:00-07:00 | 0.92474 | 2.4834 | 0.86137 | 0.88345 | 2.4491
2022-02-28 | 08:45:00-07:00 | 1.3062 | 1.6416 | 0.98032 | 1.274 | 1.7303
2022-03-08 | 16:00:00-07:00 | 0.94251 | 2.553 | 1.5122 | 0.70014 | 6.7366
2022-03-16 | 19:15:00-07:00 | 1.1352 | 5.2866 | 1.1276 | 0.9514 | 1.7503
2022-03-23 | 12:15:00-07:00 | 1.0186 | 0.92873 | 1.1533 | 1.0136 | 1.5199
2022-03-30 | 05:15:00-07:00 | 1.0474 | 0.60912 | 0.77907 | 1.2124 | 0.84426
2022-04-05 | 22:30:00-07:00 | 1.1579 | 0.92661 | 1.0741 | 1.2591 | 0.68922
2022-04-15 | 00:15:00-07:00 | 1.0384 | 0.85759 | 1.1378 | 1.1372 | 0.74122
2022-04-21 | 17:15:00-07:00 | 1.8063 | 1.053 | 0.92902 | 1.349 | 0.67614
2022-04-28 | 10:30:00-07:00 | 2.0041 | 4.7474 | 1.1786 | 1.7073 | 0.62157
2022-05-05 | 03:30:00-07:00 | 1.5986 | 0.7893 | 1.0526 | 1.1423 | 0.83312
2022-05-11 | 20:30:00-07:00 | 1.6812 | 0.81656 | 1.6944 | 1.5069 | 0.98667
2022-05-18 | 13:45:00-07:00 | 1.2863 | 5.1215 | 1.2396 | 1.1346 | 1.335
2022-05-25 | 07:15:00-07:00 | 1.1589 | 0.95369 | 0.87967 | 1.2939 | 1.2299

## SAM_TMY2020_row8
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio | Albedo_actual
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70434 | 0.71297 | 0.014518 | 1.0122 | 815.377 | 24.6902 | 2.5534 | 1.1062 | 0.20104
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.70617 | 0.7062 | 0.014732 | 1 | 815.377 | 24.6902 | 2.5534 | 1.0064 | 0.21465
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.70694 | 0.69344 | 0.010248 | 0.98091 | 815.377 | 24.6902 | 2.5534 | 0.91649 | 0.20108
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70669 | 0.70161 | 0.014994 | 0.99281 | 815.377 | 24.6902 | 2.5534 | 1.1044 | 0.18924
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.68433 | 0.67739 | 0.016735 | 0.98986 | 790.957 | 26.7545 | 2.4147 | 1.0617 | 0.20199
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.68144 | 0.67914 | 0.015025 | 0.99663 | 790.957 | 26.7545 | 2.4147 | 0.9922 | 0.19409
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.68293 | 0.66349 | 0.018728 | 0.97153 | 790.957 | 26.7545 | 2.4147 | 1.1624 | 0.19023
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.68287 | 0.66911 | 0.013027 | 0.97985 | 790.957 | 26.7545 | 2.4147 | 1.0223 | 0.18185
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.58702 | 0.58343 | 0.016668 | 0.99389 | 669.655 | 25.4276 | 2.3727 | 1.0985 | 0.18577
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.58228 | 0.58557 | 0.014935 | 1.0057 | 669.655 | 25.4276 | 2.3727 | 1.1618 | 0.18466
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.58339 | 0.58655 | 0.011753 | 1.0054 | 669.655 | 25.4276 | 2.3727 | 1.14 | 0.17984
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.58639 | 0.58857 | 0.011675 | 1.0037 | 669.655 | 25.4276 | 2.3727 | 1.1966 | 0.20006
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.58468 | 0.57709 | 0.017043 | 0.98702 | 669.655 | 25.4276 | 2.3727 | 1.1745 | 0.21052
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.64586 | 0.62911 | 0.0099971 | 0.97408 | 720.547 | 20.9691 | 2.4432 | 1.1121 | 0.21541
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.64659 | 0.62762 | 0.014119 | 0.97066 | 720.547 | 20.9691 | 2.4432 | 0.96336 | 0.22237
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.6402 | 0.64176 | 0.019262 | 1.0024 | 720.547 | 20.9691 | 2.4432 | 1.276 | 0.21775
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.64135 | 0.63772 | 0.020594 | 0.99434 | 720.547 | 20.9691 | 2.4432 | 0.9354 | 0.21258
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.56966 | 0.56157 | 0.01306 | 0.98581 | 611.291 | 14.2291 | 2.7405 | 1.1945 | 0.2226
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.56776 | 0.56915 | 0.014471 | 1.0025 | 611.291 | 14.2291 | 2.7405 | 1.0724 | 0.22062
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.56942 | 0.5709 | 0.010647 | 1.0026 | 611.291 | 14.2291 | 2.7405 | 1.11 | 0.22259
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.57118 | 0.56716 | 0.013559 | 0.99296 | 611.291 | 14.2291 | 2.7405 | 0.97089 | 0.22689
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.48866 | 0.4825 | 0.0094922 | 0.98741 | 513.208 | 8.4866 | 2.5476 | 0.98877 | 0.22736
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.491 | 0.49384 | 0.0089041 | 1.0058 | 513.208 | 8.4866 | 2.5476 | 1.1413 | 0.22352
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.49391 | 0.48942 | 0.0050927 | 0.99091 | 513.208 | 8.4866 | 2.5476 | 1.1315 | 0.24139
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.4908 | 0.494 | 0.0078651 | 1.0065 | 513.208 | 8.4866 | 2.5476 | 0.99471 | 0.26171
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.49486 | 0.49311 | 0.0073566 | 0.99646 | 513.208 | 8.4866 | 2.5476 | 1.1644 | 0.23359
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.41575 | 0.41702 | 0.0071756 | 1.0031 | 421.538 | 3.3412 | 3.1782 | 1.1084 | 0.29322
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.41469 | 0.41611 | 0.0054051 | 1.0034 | 421.538 | 3.3412 | 3.1782 | 1.2695 | 0.2338
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.41512 | 0.41804 | 0.0045589 | 1.007 | 421.538 | 3.3412 | 3.1782 | 1.1765 | 0.24579
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.41446 | 0.4184 | 0.0051556 | 1.0095 | 421.538 | 3.3412 | 3.1782 | 1.1678 | 0.44009
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.42189 | 0.4211 | 0.0042157 | 0.99812 | 428.325 | 2.1398 | 2.3806 | 1.1643 | 0.60833
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.41846 | 0.42474 | 0.0083584 | 1.015 | 428.325 | 2.1398 | 2.3806 | 1.0223 | 0.32067
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.42298 | 0.41406 | 0.0040214 | 0.97891 | 428.325 | 2.1398 | 2.3806 | 0.96075 | 0.26609
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.41985 | 0.42433 | 0.0053797 | 1.0107 | 428.325 | 2.1398 | 2.3806 | 1.6316 | 0.63986
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.41903 | 0.41367 | 0.0077315 | 0.9872 | 428.325 | 2.1398 | 2.3806 | 1.2878 | 0.64239
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.50952 | 0.50799 | 0.0057752 | 0.99699 | 519.153 | 3.06 | 3.1041 | 1.3707 | 0.39554
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.50348 | 0.51197 | 0.0076525 | 1.0169 | 519.153 | 3.06 | 3.1041 | 1.3686 | 0.3917
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.50387 | 0.51022 | 0.0091823 | 1.0126 | 519.153 | 3.06 | 3.1041 | 1.0647 | 0.39736
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.50778 | 0.51639 | 0.01341 | 1.017 | 519.153 | 3.06 | 3.1041 | 1.3493 | 0.42006
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.6026 | 0.60336 | 0.0087986 | 1.0013 | 630.886 | 5.2134 | 3.0028 | 1.0803 | 0.36541
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.59955 | 0.61167 | 0.010867 | 1.0202 | 630.886 | 5.2134 | 3.0028 | 1.1412 | 0.39193
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.59945 | 0.60848 | 0.010492 | 1.0151 | 630.886 | 5.2134 | 3.0028 | 0.96151 | 0.16776
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.60359 | 0.59478 | 0.010787 | 0.98539 | 630.886 | 5.2134 | 3.0028 | 1.0102 | 0.17874
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.57289 | 0.57436 | 0.01202 | 1.0026 | 606.561 | 9.9782 | 3.4138 | 1.0913 | 0.18798
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.57171 | 0.57676 | 0.010731 | 1.0088 | 606.561 | 9.9782 | 3.4138 | 1.1396 | 0.19201
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.5714 | 0.5832 | 0.018231 | 1.0206 | 606.561 | 9.9782 | 3.4138 | 1.2531 | 0.1907
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.57315 | 0.56784 | 0.021376 | 0.99075 | 606.561 | 9.9782 | 3.4138 | 0.95894 | 0.18178
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.59469 | 0.59457 | 0.014891 | 0.9998 | 648.471 | 14.253 | 2.8131 | 1.0667 | 0.18184
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.59757 | 0.60775 | 0.016861 | 1.017 | 648.471 | 14.253 | 2.8131 | 1.3256 | 0.18693
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.58936 | 0.59969 | 0.013222 | 1.0175 | 648.471 | 14.253 | 2.8131 | 1.1728 | 0.2797
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.59227 | 0.60775 | 0.012063 | 1.0261 | 648.471 | 14.253 | 2.8131 | 1.103 | 0.18455
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_TMY2020_row24_POA
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.73932 | 0.74147 | 0.0063251 | 1.0029 | 815.377 | 24.6902 | 2.5534 | 1.09
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.73897 | 0.73882 | 0.0051594 | 0.99979 | 815.377 | 24.6902 | 2.5534 | 0.99627
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.73945 | 0.73944 | 0.0070782 | 0.99998 | 815.377 | 24.6902 | 2.5534 | 0.90011
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.74015 | 0.74536 | 0.0068617 | 1.007 | 815.377 | 24.6902 | 2.5534 | 1.1046
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.71333 | 0.71167 | 0.0069734 | 0.99769 | 790.957 | 26.7545 | 2.4147 | 1.0484
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.71078 | 0.72103 | 0.0061016 | 1.0144 | 790.957 | 26.7545 | 2.4147 | 0.98441
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.71066 | 0.70343 | 0.010689 | 0.98982 | 790.957 | 26.7545 | 2.4147 | 1.0726
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.71076 | 0.71114 | 0.0087849 | 1.0005 | 790.957 | 26.7545 | 2.4147 | 0.99246
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.61825 | 0.62837 | 0.010082 | 1.0164 | 669.655 | 25.4276 | 2.3727 | 1.0108
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.61703 | 0.61746 | 0.0086569 | 1.0007 | 669.655 | 25.4276 | 2.3727 | 1.1071
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.61925 | 0.61899 | 0.005912 | 0.99959 | 669.655 | 25.4276 | 2.3727 | 1.0684
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.61929 | 0.61472 | 0.0070526 | 0.99261 | 669.655 | 25.4276 | 2.3727 | 1.1834
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.61856 | 0.61604 | 0.0074031 | 0.99593 | 669.655 | 25.4276 | 2.3727 | 1.0546
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.67346 | 0.66147 | 0.0048647 | 0.9822 | 720.547 | 20.9691 | 2.4432 | 1.0682
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.6715 | 0.66894 | 0.0076318 | 0.99618 | 720.547 | 20.9691 | 2.4432 | 0.97663
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.67383 | 0.68229 | 0.017565 | 1.0126 | 720.547 | 20.9691 | 2.4432 | 1.2396
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.67566 | 0.68458 | 0.0082053 | 1.0132 | 720.547 | 20.9691 | 2.4432 | 0.93962
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.59596 | 0.59738 | 0.0075678 | 1.0024 | 611.291 | 14.2291 | 2.7405 | 1.0988
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.59939 | 0.60726 | 0.0062865 | 1.0131 | 611.291 | 14.2291 | 2.7405 | 1.005
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.59758 | 0.61695 | 0.0063675 | 1.0324 | 611.291 | 14.2291 | 2.7405 | 1.0677
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.59566 | 0.60821 | 0.0075786 | 1.0211 | 611.291 | 14.2291 | 2.7405 | 1.0254
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.51103 | 0.52568 | 0.0072707 | 1.0287 | 513.208 | 8.4866 | 2.5476 | 0.94944
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.51379 | 0.5324 | 0.0083731 | 1.0362 | 513.208 | 8.4866 | 2.5476 | 1.1193
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.52286 | 0.53272 | 0.0095872 | 1.0189 | 513.208 | 8.4866 | 2.5476 | 1.2149
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.52684 | 0.52843 | 0.060865 | 1.003 | 513.208 | 8.4866 | 2.5476 | 0.92044
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.52466 | 0.52558 | 0.023159 | 1.0018 | 513.208 | 8.4866 | 2.5476 | 1.0648
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.43928 | 0.45468 | 0.014948 | 1.035 | 421.538 | 3.3412 | 3.1782 | 1.1129
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.47768 | 0.45195 | 0.051675 | 0.94613 | 421.538 | 3.3412 | 3.1782 | 1.1442
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.44155 | 0.45042 | 0.015167 | 1.0201 | 421.538 | 3.3412 | 3.1782 | 1.1829
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.43929 | 0.45292 | 0.0051784 | 1.031 | 421.538 | 3.3412 | 3.1782 | 1.086
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.45429 | 0.49638 | 0.034852 | 1.0926 | 428.325 | 2.1398 | 2.3806 | 0.96655
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.44933 | 0.48042 | 0.050643 | 1.0692 | 428.325 | 2.1398 | 2.3806 | 0.8963
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.44109 | 0.45914 | 0.012077 | 1.0409 | 428.325 | 2.1398 | 2.3806 | 1.0224
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.44646 | 0.44161 | 0.0091058 | 0.98914 | 428.325 | 2.1398 | 2.3806 | 1.6148
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.44537 | 0.46643 | 0.014899 | 1.0473 | 428.325 | 2.1398 | 2.3806 | 1.2361
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.53362 | 0.56955 | 0.008704 | 1.0673 | 519.153 | 3.06 | 3.1041 | 1.2715
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.53386 | 0.54969 | 0.0080531 | 1.0297 | 519.153 | 3.06 | 3.1041 | 1.202
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.54127 | 0.55378 | 0.023644 | 1.0231 | 519.153 | 3.06 | 3.1041 | 1.1212
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.53143 | 0.54504 | 0.015489 | 1.0256 | 519.153 | 3.06 | 3.1041 | 1.0977
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.6687 | 0.67043 | 0.025371 | 1.0026 | 630.886 | 5.2134 | 3.0028 | 1.0498
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.69483 | 0.66071 | 0.053221 | 0.95089 | 630.886 | 5.2134 | 3.0028 | 1.063
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.63746 | 0.65135 | 0.0096262 | 1.0218 | 630.886 | 5.2134 | 3.0028 | 1.044
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.63384 | 0.64145 | 0.0060251 | 1.012 | 630.886 | 5.2134 | 3.0028 | 0.92305
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.60193 | 0.60833 | 0.0089842 | 1.0106 | 606.561 | 9.9782 | 3.4138 | 1.0144
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.60244 | 0.61357 | 0.0091576 | 1.0185 | 606.561 | 9.9782 | 3.4138 | 1.0063
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.60521 | 0.61203 | 0.010206 | 1.0113 | 606.561 | 9.9782 | 3.4138 | 1.1121
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.62724 | 0.60937 | 0.048723 | 0.9715 | 606.561 | 9.9782 | 3.4138 | 0.89591
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.62887 | 0.64097 | 0.0075403 | 1.0192 | 648.471 | 14.253 | 2.8131 | 1.03
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.62994 | 0.63355 | 0.0075371 | 1.0057 | 648.471 | 14.253 | 2.8131 | 1.0912
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.65687 | 0.64351 | 0.052077 | 0.97965 | 648.471 | 14.253 | 2.8131 | 1.1392
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.62833 | 0.65405 | 0.0092238 | 1.0409 | 648.471 | 14.253 | 2.8131 | 1.0031
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_TMY2020_row24_Gtotal
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70413 | 0.69749 | 0.01268 | 0.99057 | 799.5404 | 24.37 | 2.5945 | 1.1171
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.70461 | 0.69215 | 0.013379 | 0.98232 | 799.5404 | 24.37 | 2.5945 | 1.0331
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.70441 | 0.68666 | 0.010871 | 0.9748 | 799.5404 | 24.37 | 2.5945 | 0.9027
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70642 | 0.69236 | 0.014925 | 0.98011 | 799.5404 | 24.37 | 2.5945 | 1.113
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.72219 | 0.70171 | 0.014109 | 0.97164 | 827.5098 | 26.6795 | 2.4095 | 1.0849
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.72034 | 0.70551 | 0.010975 | 0.97942 | 827.5098 | 26.6795 | 2.4095 | 1.0175
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.72318 | 0.69324 | 0.012439 | 0.9586 | 827.5098 | 26.6795 | 2.4095 | 1.1268
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.71987 | 0.69695 | 0.012167 | 0.96815 | 827.5098 | 26.6795 | 2.4095 | 1.0131
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.61922 | 0.60723 | 0.015646 | 0.98062 | 693.4789 | 25.0822 | 2.3786 | 1.0772
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.61533 | 0.60364 | 0.013497 | 0.98099 | 693.4789 | 25.0822 | 2.3786 | 1.1364
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.61587 | 0.60437 | 0.011223 | 0.98132 | 693.4789 | 25.0822 | 2.3786 | 1.1187
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.61891 | 0.60478 | 0.0093112 | 0.97716 | 693.4789 | 25.0822 | 2.3786 | 1.1032
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.61746 | 0.59702 | 0.013065 | 0.9669 | 693.4789 | 25.0822 | 2.3786 | 1.1867
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.68663 | 0.65383 | 0.009739 | 0.95223 | 758.3519 | 21.0153 | 2.4291 | 1.1032
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.68688 | 0.65586 | 0.014065 | 0.95485 | 758.3519 | 21.0153 | 2.4291 | 0.96362
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.68137 | 0.67027 | 0.017592 | 0.98371 | 758.3519 | 21.0153 | 2.4291 | 1.3022
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.68176 | 0.67003 | 0.014889 | 0.9828 | 758.3519 | 21.0153 | 2.4291 | 0.95504
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.60442 | 0.58309 | 0.011768 | 0.96471 | 637.317 | 14.1509 | 2.7565 | 1.2146
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.60142 | 0.59407 | 0.013512 | 0.98778 | 637.317 | 14.1509 | 2.7565 | 1.0904
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.60393 | 0.59633 | 0.0099046 | 0.98743 | 637.317 | 14.1509 | 2.7565 | 1.1044
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.60514 | 0.59585 | 0.011718 | 0.98465 | 637.317 | 14.1509 | 2.7565 | 0.97709
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.54915 | 0.54104 | 0.0094684 | 0.98523 | 566.4177 | 8.3115 | 2.576 | 0.97652
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.55667 | 0.546 | 0.007145 | 0.98083 | 566.4177 | 8.3115 | 2.576 | 1.1462
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.55644 | 0.54297 | 0.0072915 | 0.97579 | 566.4177 | 8.3115 | 2.576 | 1.1861
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.55238 | 0.54372 | 0.0071926 | 0.98432 | 566.4177 | 8.3115 | 2.576 | 0.91682
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.55497 | 0.54413 | 0.0062729 | 0.98047 | 566.4177 | 8.3115 | 2.576 | 1.1093
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.43307 | 0.42851 | 0.0054978 | 0.98947 | 432.218 | 3.5632 | 3.0885 | 1.04
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.43154 | 0.42713 | 0.0052382 | 0.98979 | 432.218 | 3.5632 | 3.0885 | 1.0851
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.43244 | 0.42932 | 0.0041556 | 0.99279 | 432.218 | 3.5632 | 3.0885 | 1.1216
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.43235 | 0.43353 | 0.0039032 | 1.0027 | 432.218 | 3.5632 | 3.0885 | 1.1117
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.44008 | 0.42857 | 0.0056484 | 0.97384 | 440.6495 | 2.0312 | 2.3745 | 1.1239
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.4392 | 0.42787 | 0.015857 | 0.9742 | 440.6495 | 2.0312 | 2.3745 | 0.87093
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.44146 | 0.4315 | 0.0050214 | 0.97744 | 440.6495 | 2.0312 | 2.3745 | 0.96075
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.44045 | 0.43563 | 0.0061501 | 0.98906 | 440.6495 | 2.0312 | 2.3745 | 1.4382
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.43968 | 0.4312 | 0.0096581 | 0.98072 | 440.6495 | 2.0312 | 2.3745 | 1.1568
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.54889 | 0.54348 | 0.0063253 | 0.99015 | 550.8517 | 3.0463 | 3.0887 | 1.2676
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.54412 | 0.53445 | 0.0066445 | 0.98225 | 550.8517 | 3.0463 | 3.0887 | 1.2311
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.54298 | 0.54311 | 0.0086661 | 1.0002 | 550.8517 | 3.0463 | 3.0887 | 0.88582
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.54599 | 0.5392 | 0.01254 | 0.98756 | 550.8517 | 3.0463 | 3.0887 | 1.2256
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.67036 | 0.65648 | 0.00749 | 0.9793 | 695.2192 | 5.293 | 2.9426 | 0.97508
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.66786 | 0.67322 | 0.0094979 | 1.008 | 695.2192 | 5.293 | 2.9426 | 1.069
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.66602 | 0.6721 | 0.01001 | 1.0091 | 695.2192 | 5.293 | 2.9426 | 1.0158
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.67576 | 0.66198 | 0.012156 | 0.9796 | 695.2192 | 5.293 | 2.9426 | 1.0592
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.62398 | 0.62156 | 0.012266 | 0.99611 | 655.3085 | 10.1107 | 3.3939 | 1.0914
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.62434 | 0.62434 | 0.011284 | 0.99999 | 655.3085 | 10.1107 | 3.3939 | 1.0886
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.62679 | 0.62859 | 0.013286 | 1.0029 | 655.3085 | 10.1107 | 3.3939 | 1.0549
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.62915 | 0.62192 | 0.017533 | 0.98851 | 655.3085 | 10.1107 | 3.3939 | 0.89526
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.63578 | 0.63567 | 0.011905 | 0.99984 | 683.2209 | 14.2326 | 2.8166 | 0.95284
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.63742 | 0.63341 | 0.014068 | 0.99371 | 683.2209 | 14.2326 | 2.8166 | 1.2487
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.63099 | 0.6289 | 0.01112 | 0.99668 | 683.2209 | 14.2326 | 2.8166 | 1.1093
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.63415 | 0.64048 | 0.012288 | 1.01 | 683.2209 | 14.2326 | 2.8166 | 1.0659
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_TMY2020_row24_Method4_tcorr
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.71334 | 0.72544 | 0.010631 | 1.017 | 817.8893 | 23.8696 | 1.9012
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.71496 | 0.72473 | 0.0097076 | 1.0137 | 817.8893 | 23.8696 | 1.9012
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.70831 | 0.71835 | 0.0096308 | 1.0142 | 817.8893 | 23.8696 | 1.9012
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70966 | 0.71475 | 0.011913 | 1.0072 | 817.8893 | 23.8696 | 1.9012
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.7861 | 0.79868 | 0.010239 | 1.016 | 929.2904 | 26.5496 | 1.9822
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.78506 | 0.7995 | 0.014124 | 1.0184 | 929.2904 | 26.5496 | 1.9822
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.78605 | 0.79466 | 0.013409 | 1.011 | 929.2904 | 26.5496 | 1.9822
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.78573 | 0.79577 | 0.012175 | 1.0128 | 929.2904 | 26.5496 | 1.9822
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.7448 | 0.75827 | 0.012544 | 1.0181 | 873.8643 | 26.4248 | 1.9833
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.74864 | 0.75815 | 0.01223 | 1.0127 | 873.8643 | 26.4248 | 1.9833
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.75035 | 0.75808 | 0.0097665 | 1.0103 | 873.8643 | 26.4248 | 1.9833
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.75124 | 0.75699 | 0.013701 | 1.0077 | 873.8643 | 26.4248 | 1.9833
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.75221 | 0.75464 | 0.011219 | 1.0032 | 873.8643 | 26.4248 | 1.9833
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.74635 | 0.74713 | 0.012136 | 1.001 | 851.2436 | 22.8785 | 2.0097
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.74696 | 0.74682 | 0.0096682 | 0.99981 | 851.2436 | 22.8785 | 2.0097
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.74801 | 0.74961 | 0.010019 | 1.0021 | 851.2436 | 22.8785 | 2.0097
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.74953 | 0.75185 | 0.013661 | 1.0031 | 851.2436 | 22.8785 | 2.0097
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.66882 | 0.66561 | 0.011777 | 0.9952 | 727.2704 | 15.5732 | 2.1253
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.67368 | 0.67242 | 0.010741 | 0.99813 | 727.2704 | 15.5732 | 2.1253
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.67276 | 0.67149 | 0.011637 | 0.9981 | 727.2704 | 15.5732 | 2.1253
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.67535 | 0.67545 | 0.013644 | 1.0001 | 727.2704 | 15.5732 | 2.1253
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.5366 | 0.52651 | 0.015412 | 0.98119 | 558.6976 | 11.5078 | 2.329
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.53824 | 0.53269 | 0.0079559 | 0.98969 | 558.6976 | 11.5078 | 2.329
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.53794 | 0.53131 | 0.0078045 | 0.98767 | 558.6976 | 11.5078 | 2.329
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.53992 | 0.52974 | 0.0064714 | 0.98114 | 558.6976 | 11.5078 | 2.329
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.54084 | 0.52962 | 0.0074163 | 0.97925 | 558.6976 | 11.5078 | 2.329
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.45856 | 0.44954 | 0.006926 | 0.98032 | 465.0211 | 6.9316 | 2.5407
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.45835 | 0.44997 | 0.00547 | 0.98171 | 465.0211 | 6.9316 | 2.5407
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.46006 | 0.45023 | 0.0047369 | 0.97862 | 465.0211 | 6.9316 | 2.5407
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.4605 | 0.44998 | 0.0049628 | 0.97716 | 465.0211 | 6.9316 | 2.5407
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.50878 | 0.49347 | 0.0065234 | 0.9699 | 511.1755 | 4.5458 | 1.8923
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.50358 | 0.49341 | 0.0061288 | 0.9798 | 511.1755 | 4.5458 | 1.8923
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.5052 | 0.48801 | 0.0068186 | 0.96598 | 511.1755 | 4.5458 | 1.8923
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.50156 | 0.49881 | 0.012056 | 0.99452 | 511.1755 | 4.5458 | 1.8923
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.49678 | 0.48767 | 0.011155 | 0.98165 | 511.1755 | 4.5458 | 1.8923
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.69101 | 0.68646 | 0.0083908 | 0.99342 | 711.9797 | 1.7095 | 2.2889
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.69735 | 0.68871 | 0.008292 | 0.98762 | 711.9797 | 1.7095 | 2.2889
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.68869 | 0.68949 | 0.0081597 | 1.0012 | 711.9797 | 1.7095 | 2.2889
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.69481 | 0.68858 | 0.0096105 | 0.99104 | 711.9797 | 1.7095 | 2.2889
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.5633 | 0.55091 | 0.015414 | 0.97801 | 580.1866 | 7.2296 | 2.4358
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.55722 | 0.5564 | 0.011612 | 0.99854 | 580.1866 | 7.2296 | 2.4358
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.55434 | 0.56125 | 0.011562 | 1.0125 | 580.1866 | 7.2296 | 2.4358
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.55938 | 0.55483 | 0.008468 | 0.99186 | 580.1866 | 7.2296 | 2.4358
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.7892 | 0.79033 | 0.0097 | 1.0014 | 856.1546 | 11.7973 | 3.2196
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.79246 | 0.79149 | 0.012146 | 0.99878 | 856.1546 | 11.7973 | 3.2196
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.79393 | 0.79541 | 0.0094349 | 1.0019 | 856.1546 | 11.7973 | 3.2196
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.78927 | 0.78916 | 0.011394 | 0.99986 | 856.1546 | 11.7973 | 3.2196
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.5822 | 0.58475 | 0.011595 | 1.0044 | 629.3758 | 15.7084 | 2.4638
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.59366 | 0.5913 | 0.015572 | 0.99602 | 629.3758 | 15.7084 | 2.4638
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.58602 | 0.58158 | 0.012448 | 0.99242 | 629.3758 | 15.7084 | 2.4638
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.5794 | 0.58415 | 0.010813 | 1.0082 | 629.3758 | 15.7084 | 2.4638
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_TMY2020_row24_Method4
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70413 | 0.70836 | 0.012005 | 1.006 | 799.5404 | 24.37 | 2.5945
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.70461 | 0.70845 | 0.013179 | 1.0055 | 799.5404 | 24.37 | 2.5945
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.70441 | 0.70046 | 0.010614 | 0.9944 | 799.5404 | 24.37 | 2.5945
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70642 | 0.69456 | 0.014134 | 0.98322 | 799.5404 | 24.37 | 2.5945
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.72219 | 0.71385 | 0.014027 | 0.98845 | 827.5098 | 26.6795 | 2.4095
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.72034 | 0.71498 | 0.010936 | 0.99256 | 827.5098 | 26.6795 | 2.4095
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.72318 | 0.71007 | 0.013123 | 0.98188 | 827.5098 | 26.6795 | 2.4095
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.71987 | 0.71044 | 0.012277 | 0.9869 | 827.5098 | 26.6795 | 2.4095
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.61922 | 0.61596 | 0.015163 | 0.99472 | 693.4789 | 25.0822 | 2.3786
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.61533 | 0.61672 | 0.013223 | 1.0023 | 693.4789 | 25.0822 | 2.3786
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.61587 | 0.61651 | 0.011706 | 1.001 | 693.4789 | 25.0822 | 2.3786
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.61891 | 0.61504 | 0.010147 | 0.99374 | 693.4789 | 25.0822 | 2.3786
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.61746 | 0.6103 | 0.012237 | 0.98841 | 693.4789 | 25.0822 | 2.3786
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.68663 | 0.67255 | 0.0098752 | 0.97949 | 758.3519 | 21.0153 | 2.4291
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.68688 | 0.67207 | 0.013605 | 0.97845 | 758.3519 | 21.0153 | 2.4291
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.68137 | 0.67737 | 0.019262 | 0.99414 | 758.3519 | 21.0153 | 2.4291
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.68176 | 0.67694 | 0.015107 | 0.99293 | 758.3519 | 21.0153 | 2.4291
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.60442 | 0.59115 | 0.010584 | 0.97804 | 637.317 | 14.1509 | 2.7565
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.60142 | 0.59934 | 0.014576 | 0.99655 | 637.317 | 14.1509 | 2.7565
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.60393 | 0.59833 | 0.0096279 | 0.99074 | 637.317 | 14.1509 | 2.7565
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.60514 | 0.6013 | 0.011808 | 0.99365 | 637.317 | 14.1509 | 2.7565
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.54915 | 0.53994 | 0.0090494 | 0.98323 | 566.4177 | 8.3115 | 2.576
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.55667 | 0.54815 | 0.0070754 | 0.9847 | 566.4177 | 8.3115 | 2.576
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.55644 | 0.54579 | 0.0072566 | 0.98086 | 566.4177 | 8.3115 | 2.576
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.55238 | 0.54388 | 0.0072661 | 0.9846 | 566.4177 | 8.3115 | 2.576
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.55497 | 0.54399 | 0.0060655 | 0.98022 | 566.4177 | 8.3115 | 2.576
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.43307 | 0.42631 | 0.0062369 | 0.98439 | 432.218 | 3.5632 | 3.0885
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.43154 | 0.42621 | 0.0048426 | 0.98766 | 432.218 | 3.5632 | 3.0885
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.43244 | 0.42746 | 0.0039571 | 0.9885 | 432.218 | 3.5632 | 3.0885
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.43235 | 0.42726 | 0.0039583 | 0.98823 | 432.218 | 3.5632 | 3.0885
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.44008 | 0.43385 | 0.0054627 | 0.98584 | 440.6495 | 2.0312 | 2.3745
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.4392 | 0.43463 | 0.016074 | 0.98959 | 440.6495 | 2.0312 | 2.3745
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.44146 | 0.43638 | 0.0051335 | 0.98849 | 440.6495 | 2.0312 | 2.3745
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.44045 | 0.43659 | 0.00621 | 0.99123 | 440.6495 | 2.0312 | 2.3745
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.43926 | 0.42833 | 0.010144 | 0.97512 | 440.6495 | 2.0312 | 2.3745
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.54889 | 0.54225 | 0.0062703 | 0.98791 | 550.8517 | 3.0463 | 3.0887
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.54412 | 0.54246 | 0.0068894 | 0.99695 | 550.8517 | 3.0463 | 3.0887
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.54298 | 0.54696 | 0.0087678 | 1.0073 | 550.8517 | 3.0463 | 3.0887
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.54599 | 0.54812 | 0.01254 | 1.0039 | 550.8517 | 3.0463 | 3.0887
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.67036 | 0.66488 | 0.008094 | 0.99183 | 695.2192 | 5.293 | 2.9426
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.66786 | 0.66905 | 0.0093731 | 1.0018 | 695.2192 | 5.293 | 2.9426
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.66602 | 0.67939 | 0.009756 | 1.0201 | 695.2192 | 5.293 | 2.9426
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.67576 | 0.66506 | 0.012129 | 0.98416 | 695.2192 | 5.293 | 2.9426
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.62398 | 0.62219 | 0.012675 | 0.99714 | 655.3085 | 10.1107 | 3.3939
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.62434 | 0.62433 | 0.010367 | 0.99998 | 655.3085 | 10.1107 | 3.3939
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.62679 | 0.62681 | 0.013157 | 1 | 655.3085 | 10.1107 | 3.3939
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.62915 | 0.62044 | 0.017608 | 0.98617 | 655.3085 | 10.1107 | 3.3939
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.63578 | 0.63577 | 0.012076 | 1 | 683.2209 | 14.2326 | 2.8166
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.63742 | 0.639 | 0.015537 | 1.0025 | 683.2209 | 14.2326 | 2.8166
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.63099 | 0.63029 | 0.011326 | 0.99889 | 683.2209 | 14.2326 | 2.8166
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.63415 | 0.63231 | 0.012896 | 0.99709 | 683.2209 | 14.2326 | 2.8166
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_TMYA01_POA
DATE FROM ISO | Column1 | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel | IECratio
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.74916 | 0.74808 | 0.0070985 | 0.99856 | 824.628 | 24.7768 | 2.5208 | 1.0808
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.75154 | 0.74554 | 0.0052893 | 0.99202 | 824.628 | 24.7768 | 2.5208 | 0.97988
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.75207 | 0.74638 | 0.0078281 | 0.99244 | 824.628 | 24.7768 | 2.5208 | 0.89527
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.75028 | 0.75181 | 0.0070699 | 1.002 | 824.628 | 24.7768 | 2.5208 | 1.0765
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.71669 | 0.71251 | 0.0067542 | 0.99417 | 792.077 | 26.791 | 2.4155 | 1.036
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.71598 | 0.72192 | 0.0066073 | 1.0083 | 792.077 | 26.791 | 2.4155 | 0.96595
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.71615 | 0.70429 | 0.011008 | 0.98343 | 792.077 | 26.791 | 2.4155 | 1.0612
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.71467 | 0.71199 | 0.0088464 | 0.99624 | 792.077 | 26.791 | 2.4155 | 0.98129
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.62183 | 0.62955 | 0.012724 | 1.0124 | 671.098 | 25.4276 | 2.3727 | 1.0007
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.62013 | 0.61861 | 0.010049 | 0.99754 | 671.098 | 25.4276 | 2.3727 | 1.0948
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.62193 | 0.62017 | 0.0064368 | 0.99718 | 671.098 | 25.4276 | 2.3727 | 1.0662
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.6236 | 0.61597 | 0.0080478 | 0.98777 | 671.098 | 25.4276 | 2.3727 | 1.178
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.62441 | 0.61702 | 0.0093493 | 0.98817 | 671.098 | 25.4276 | 2.3727 | 1.0567
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.67301 | 0.65696 | 0.0064826 | 0.97615 | 715.047 | 20.8755 | 2.421 | 1.0555
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.66985 | 0.66444 | 0.0080154 | 0.99191 | 715.047 | 20.8755 | 2.421 | 0.93994
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.67504 | 0.67769 | 0.02005 | 1.0039 | 715.047 | 20.8755 | 2.421 | 1.2218
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.67604 | 0.68002 | 0.0095358 | 1.0059 | 715.047 | 20.8755 | 2.421 | 0.9303
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.5997 | 0.59619 | 0.0095752 | 0.99416 | 609.856 | 14.1965 | 2.745 | 1.1292
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.60564 | 0.60607 | 0.013058 | 1.0007 | 609.856 | 14.1965 | 2.745 | 1.0084
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.60374 | 0.61579 | 0.011249 | 1.02 | 609.856 | 14.1965 | 2.745 | 1.0636
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.60114 | 0.60694 | 0.013289 | 1.0096 | 609.856 | 14.1965 | 2.745 | 0.99566
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.50088 | 0.51547 | 0.012305 | 1.0291 | 502.057 | 8.5 | 2.5532 | 0.92029
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.5082 | 0.52201 | 0.013027 | 1.0272 | 502.057 | 8.5 | 2.5532 | 1.07
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.51915 | 0.52204 | 0.011385 | 1.0056 | 502.057 | 8.5 | 2.5532 | 1.1407
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.52426 | 0.51987 | 0.018052 | 0.99163 | 502.057 | 8.5 | 2.5532 | 1.0073
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.52003 | 0.51512 | 0.015479 | 0.99054 | 502.057 | 8.5 | 2.5532 | 1.0635
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.44767 | 0.45621 | 0.014964 | 1.0191 | 422.989 | 3.4327 | 3.1439 | 1.091
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.44606 | 0.45324 | 0.025852 | 1.0161 | 422.989 | 3.4327 | 3.1439 | 1.1105
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.4397 | 0.45175 | 0.014663 | 1.0274 | 422.989 | 3.4327 | 3.1439 | 1.0982
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.44361 | 0.45421 | 0.014956 | 1.0239 | 422.989 | 3.4327 | 3.1439 | 1.095
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.45558 | 0.49884 | 0.02433 | 1.095 | 430.677 | 2.2391 | 2.3696 | 1.2049
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.45035 | 0.48205 | 0.054271 | 1.0704 | 430.677 | 2.2391 | 2.3696 | 0.84875
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.4473 | 0.46167 | 0.012769 | 1.0321 | 430.677 | 2.2391 | 2.3696 | 1.043
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.46208 | 0.44398 | 0.028011 | 0.96081 | 430.677 | 2.2391 | 2.3696 | 1.657
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.45221 | 0.46851 | 0.046443 | 1.036 | 430.677 | 2.2391 | 2.3696 | 1.3628
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.56632 | 0.588 | 0.056988 | 1.0383 | 535.699 | 2.9492 | 3.0928 | 1.3162
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.55288 | 0.56588 | 0.016818 | 1.0235 | 535.699 | 2.9492 | 3.0928 | 1.2192
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.56817 | 0.57426 | 0.017275 | 1.0107 | 535.699 | 2.9492 | 3.0928 | 0.96846
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.54864 | 0.56567 | 0.020422 | 1.031 | 535.699 | 2.9492 | 3.0928 | 1.0529
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.71205 | 0.67981 | 0.050351 | 0.95472 | 644.341 | 5.2231 | 2.9924 | 1.0007
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.65997 | 0.67385 | 0.016527 | 1.021 | 644.341 | 5.2231 | 2.9924 | 1.178
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.64522 | 0.66331 | 0.0080922 | 1.028 | 644.341 | 5.2231 | 2.9924 | 1.0618
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.64638 | 0.65306 | 0.0052192 | 1.0103 | 644.341 | 5.2231 | 2.9924 | 1.0024
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.59931 | 0.60141 | 0.0087993 | 1.0035 | 598.574 | 9.9307 | 3.4175 | 0.99719
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.59746 | 0.60699 | 0.0073181 | 1.0159 | 598.574 | 9.9307 | 3.4175 | 0.98644
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.59877 | 0.60479 | 0.0098024 | 1.01 | 598.574 | 9.9307 | 3.4175 | 1.0233
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.60184 | 0.60217 | 0.0086799 | 1.0005 | 598.574 | 9.9307 | 3.4175 | 0.91756
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.63424 | 0.64363 | 0.0070194 | 1.0148 | 651.465 | 14.2492 | 2.8128 | 1.0015
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.63467 | 0.63632 | 0.0059361 | 1.0026 | 651.465 | 14.2492 | 2.8128 | 1.0487
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.63838 | 0.6463 | 0.015901 | 1.0124 | 651.465 | 14.2492 | 2.8128 | 1.1664
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.63545 | 0.65624 | 0.0096854 | 1.0327 | 651.465 | 14.2492 | 2.8128 | 0.9772
Formulas:
DATE FROM ISO = DATEVALUE(MID([Column1],1,10))+TIMEVALUE(MID([Column1],12,5))+TIME(MID([Column1],18,2),0,0)

## SAM_S02_row24_POA
DATE FROM ISO |  | SAM_test | DAS_test | SAM_model_1sigma_pct | ratio | poa | t_amb | w_vel
2021-06-07 17:00 | 2021-06-07 17:00:00-07:00 | 0.70853 | 0.70606 | 0.0056092 | 0.99651 | 776.236 | 23.7712 | 1.9095
2021-06-14 10:00 | 2021-06-14 10:00:00-07:00 | 0.70958 | 0.70501 | 0.0062542 | 0.99357 | 776.236 | 23.7712 | 1.9095
2021-06-21 03:15 | 2021-06-21 03:15:00-07:00 | 0.71037 | 0.70774 | 0.010332 | 0.99631 | 776.236 | 23.7712 | 1.9095
2021-06-29 17:45 | 2021-06-29 17:45:00-07:00 | 0.70919 | 0.71044 | 0.0096959 | 1.0018 | 776.236 | 23.7712 | 1.9095
2021-07-07 14:30 | 2021-07-07 14:30:00-07:00 | 0.78099 | 0.77874 | 0.0059696 | 0.99711 | 882.592 | 26.5955 | 1.9709
2021-07-14 07:30 | 2021-07-14 07:30:00-07:00 | 0.7836 | 0.7889 | 0.0086976 | 1.0068 | 882.592 | 26.5955 | 1.9709
2021-07-21 00:30 | 2021-07-21 00:30:00-07:00 | 0.78222 | 0.77008 | 0.0090068 | 0.98449 | 882.592 | 26.5955 | 1.9709
2021-07-28 13:30 | 2021-07-28 13:30:00-07:00 | 0.78166 | 0.77673 | 0.006972 | 0.99368 | 882.592 | 26.5955 | 1.9709
2021-08-04 06:45 | 2021-08-04 06:45:00-07:00 | 0.73717 | 0.74673 | 0.012964 | 1.013 | 824.323 | 26.5336 | 2.0233
2021-08-10 23:45 | 2021-08-10 23:45:00-07:00 | 0.73863 | 0.73548 | 0.0080908 | 0.99574 | 824.323 | 26.5336 | 2.0233
2021-08-17 16:45 | 2021-08-17 16:45:00-07:00 | 0.73931 | 0.73583 | 0.0069146 | 0.99529 | 824.323 | 26.5336 | 2.0233
2021-08-24 13:30 | 2021-08-24 13:30:00-07:00 | 0.73799 | 0.73242 | 0.0073999 | 0.99246 | 824.323 | 26.5336 | 2.0233
2021-08-31 06:30 | 2021-08-31 06:30:00-07:00 | 0.74286 | 0.73515 | 0.0079177 | 0.98963 | 824.323 | 26.5336 | 2.0233
2021-09-06 23:30 | 2021-09-06 23:30:00-07:00 | 0.74564 | 0.73263 | 0.0090742 | 0.98256 | 814.178 | 23.1048 | 2.0073
2021-09-13 17:00 | 2021-09-13 17:00:00-07:00 | 0.74623 | 0.73902 | 0.0085213 | 0.99034 | 814.178 | 23.1048 | 2.0073
2021-09-20 10:00 | 2021-09-20 10:00:00-07:00 | 0.74636 | 0.74597 | 0.010402 | 0.99948 | 814.178 | 23.1048 | 2.0073
2021-09-28 01:30 | 2021-09-28 01:30:00-07:00 | 0.74939 | 0.74996 | 0.011272 | 1.0008 | 814.178 | 23.1048 | 2.0073
2021-10-04 18:30 | 2021-10-04 18:30:00-07:00 | 0.67815 | 0.66909 | 0.012708 | 0.98663 | 703.194 | 16.1264 | 2.1092
2021-10-11 11:30 | 2021-10-11 11:30:00-07:00 | 0.68275 | 0.68004 | 0.015481 | 0.99603 | 703.194 | 16.1264 | 2.1092
2021-10-18 04:30 | 2021-10-18 04:30:00-07:00 | 0.68047 | 0.68428 | 0.013466 | 1.0056 | 703.194 | 16.1264 | 2.1092
2021-10-27 16:30 | 2021-10-27 16:30:00-07:00 | 0.68252 | 0.68316 | 0.025166 | 1.0009 | 703.194 | 16.1264 | 2.1092
2021-11-03 09:30 | 2021-11-03 09:30:00-07:00 | 0.53031 | 0.53753 | 0.021352 | 1.0136 | 531.017 | 11.6822 | 2.308
2021-11-10 02:30 | 2021-11-10 02:30:00-07:00 | 0.54098 | 0.54343 | 0.016205 | 1.0045 | 531.017 | 11.6822 | 2.308
2021-11-16 19:30 | 2021-11-16 19:30:00-07:00 | 0.54136 | 0.5431 | 0.015053 | 1.0032 | 531.017 | 11.6822 | 2.308
2021-11-23 13:00 | 2021-11-23 13:00:00-07:00 | 0.53611 | 0.54093 | 0.024281 | 1.009 | 531.017 | 11.6822 | 2.308
2021-11-30 06:00 | 2021-11-30 06:00:00-07:00 | 0.53271 | 0.53698 | 0.024268 | 1.008 | 531.017 | 11.6822 | 2.308
2021-12-06 23:15 | 2021-12-06 23:15:00-07:00 | 0.46317 | 0.46641 | 0.018464 | 1.007 | 443.633 | 8.0486 | 2.3481
2021-12-13 16:15 | 2021-12-13 16:15:00-07:00 | 0.46443 | 0.46724 | 0.022304 | 1.006 | 443.633 | 8.0486 | 2.3481
2021-12-20 09:15 | 2021-12-20 09:15:00-07:00 | 0.45512 | 0.46478 | 0.019594 | 1.0212 | 443.633 | 8.0486 | 2.3481
2021-12-27 02:45 | 2021-12-27 02:45:00-07:00 | 0.46026 | 0.4676 | 0.02146 | 1.016 | 443.633 | 8.0486 | 2.3481
2022-01-02 19:45 | 2022-01-02 19:45:00-07:00 | 0.49981 | 0.53135 | 0.046766 | 1.0631 | 465.967 | 4.544 | 1.8323
2022-01-09 13:00 | 2022-01-09 13:00:00-07:00 | 0.50674 | 0.5141 | 0.041676 | 1.0145 | 465.967 | 4.544 | 1.8323
2022-01-16 06:00 | 2022-01-16 06:00:00-07:00 | 0.488 | 0.4947 | 0.022295 | 1.0137 | 465.967 | 4.544 | 1.8323
2022-01-22 23:00 | 2022-01-22 23:00:00-07:00 | 0.48261 | 0.48191 | 0.041019 | 0.99855 | 465.967 | 4.544 | 1.8323
2022-01-29 16:00 | 2022-01-29 16:00:00-07:00 | 0.50153 | 0.49835 | 0.049791 | 0.99365 | 465.967 | 4.544 | 1.8323
2022-02-05 09:00 | 2022-02-05 09:00:00-07:00 | 0.6862 | 0.71202 | 0.04055 | 1.0376 | 654.071 | 1.5972 | 2.222
2022-02-12 02:00 | 2022-02-12 02:00:00-07:00 | 0.67538 | 0.68185 | 0.019099 | 1.0096 | 654.071 | 1.5972 | 2.222
2022-02-18 19:30 | 2022-02-18 19:30:00-07:00 | 0.68715 | 0.70432 | 0.024628 | 1.025 | 654.071 | 1.5972 | 2.222
2022-02-28 08:45 | 2022-02-28 08:45:00-07:00 | 0.67731 | 0.68959 | 0.017034 | 1.0181 | 654.071 | 1.5972 | 2.222
2022-03-08 16:00 | 2022-03-08 16:00:00-07:00 | 0.52968 | 0.52166 | 0.085199 | 0.98487 | 492.688 | 7.1792 | 2.4514
2022-03-16 19:15 | 2022-03-16 19:15:00-07:00 | 0.50224 | 0.52159 | 0.017916 | 1.0385 | 492.688 | 7.1792 | 2.4514
2022-03-23 12:15 | 2022-03-23 12:15:00-07:00 | 0.50063 | 0.51451 | 0.014503 | 1.0277 | 492.688 | 7.1792 | 2.4514
2022-03-30 05:15 | 2022-03-30 05:15:00-07:00 | 0.50613 | 0.50839 | 0.0094367 | 1.0045 | 492.688 | 7.1792 | 2.4514
2022-04-05 22:30 | 2022-04-05 22:30:00-07:00 | 0.79854 | 0.79285 | 0.0073103 | 0.99288 | 830.988 | 11.9278 | 3.2838
2022-04-15 00:15 | 2022-04-15 00:15:00-07:00 | 0.80197 | 0.80357 | 0.0064401 | 1.002 | 830.988 | 11.9278 | 3.2838
2022-04-21 17:15 | 2022-04-21 17:15:00-07:00 | 0.80049 | 0.80195 | 0.0070096 | 1.0018 | 830.988 | 11.9278 | 3.2838
2022-04-28 10:30 | 2022-04-28 10:30:00-07:00 | 0.79783 | 0.79957 | 0.0063224 | 1.0022 | 830.988 | 11.9278 | 3.2838
2022-05-05 03:30 | 2022-05-05 03:30:00-07:00 | 0.59981 | 0.60799 | 0.0083773 | 1.0136 | 618.299 | 15.7917 | 2.4727
2022-05-11 20:30 | 2022-05-11 20:30:00-07:00 | 0.59835 | 0.60402 | 0.0099163 | 1.0095 | 618.299 | 15.7917 | 2.4727
2022-05-18 13:45 | 2022-05-18 13:45:00-07:00 | 0.60708 | 0.60912 | 0.012671 | 1.0034 | 618.299 | 15.7917 | 2.4727
2022-05-25 07:15 | 2022-05-25 07:15:00-07:00 | 0.60259 | 0.61977 | 0.011947 | 1.0285 | 618.299 | 15.7917 | 2.4727